## Field list
NOTE: Use unit-id 100 for the com.victronenergy.system data, for more information see FAQ. |  |  |  | ModbusTCP Register list
dbus-service-name | description | Address | Type | Scalefactor | Range | dbus-obj-path | writable | dbus-unit | Remarks
com.victronenergy.system | Serial (System) | 800 | string[6] | 1 | 12 characters | /Serial | no |  | System value -> MAC address of CCGX (represented as string)
com.victronenergy.system | CCGX Relay 1 state | 806 | uint16 | 1 | 0 to 1 | /Relay/0/State | yes | 0=Open;1=Closed
com.victronenergy.system | CCGX Relay 2 state | 807 | uint16 | 1 | 0 to 1 | /Relay/1/State | yes | 0=Open;1=Closed | Relay 1 is available on Venus GX only.
com.victronenergy.system | PV - AC-coupled on output L1 | 808 | uint16 | 1 | 0 to 65536 | /Ac/PvOnOutput/L1/Power | no | W | Summation of all AC-Coupled PV Inverters on the output
com.victronenergy.system | PV - AC-coupled on output L2 | 809 | uint16 | 1 | 0 to 65536 | /Ac/PvOnOutput/L2/Power | no | W
com.victronenergy.system | PV - AC-coupled on output L3 | 810 | uint16 | 1 | 0 to 65536 | /Ac/PvOnOutput/L3/Power | no | W
com.victronenergy.system | PV - AC-coupled on input L1 | 811 | uint16 | 1 | 0 to 65536 | /Ac/PvOnGrid/L1/Power | no | W | Summation of all AC-Coupled PV Inverters on the input
com.victronenergy.system | PV - AC-coupled on input L2 | 812 | uint16 | 1 | 0 to 65536 | /Ac/PvOnGrid/L2/Power | no | W
com.victronenergy.system | PV - AC-coupled on input L3 | 813 | uint16 | 1 | 0 to 65536 | /Ac/PvOnGrid/L3/Power | no | W
com.victronenergy.system | PV - AC-coupled on generator L1 | 814 | uint16 | 1 | 0 to 65536 | /Ac/PvOnGenset/L1/Power | no | W | Summation of all AC-Coupled PV Inverters on a generator. Bit theoretic; this will never be used.
com.victronenergy.system | PV - AC-coupled on generator L2 | 815 | uint16 | 1 | 0 to 65536 | /Ac/PvOnGenset/L2/Power | no | W
com.victronenergy.system | PV - AC-coupled on generator L3 | 816 | uint16 | 1 | 0 to 65536 | /Ac/PvOnGenset/L3/Power | no | W
com.victronenergy.system | AC Consumption L1 | 817 | uint16 | 1 | 0 to 65536 | /Ac/Consumption/L1/Power | no | W | Power supplied by system to loads.
com.victronenergy.system | AC Consumption L2 | 818 | uint16 | 1 | 0 to 65536 | /Ac/Consumption/L2/Power | no | W
com.victronenergy.system | AC Consumption L3 | 819 | uint16 | 1 | 0 to 65536 | /Ac/Consumption/L3/Power | no | W
com.victronenergy.system | Grid L1 | 820 | int16 | 1 | -32768 to 32767 | /Ac/Grid/L1/Power | no | W | Power supplied by Grid to system.
com.victronenergy.system | Grid L2 | 821 | int16 | 1 | -32768 to 32767 | /Ac/Grid/L2/Power | no | W
com.victronenergy.system | Grid L3 | 822 | int16 | 1 | -32768 to 32767 | /Ac/Grid/L3/Power | no | W
com.victronenergy.system | Genset L1 | 823 | int16 | 1 | -32768 to 32767 | /Ac/Genset/L1/Power | no | W | Power supplied by Genset tot system.
com.victronenergy.system | Genset L2 | 824 | int16 | 1 | -32768 to 32767 | /Ac/Genset/L2/Power | no | W
com.victronenergy.system | Genset L3 | 825 | int16 | 1 | -32768 to 32767 | /Ac/Genset/L3/Power | no | W
com.victronenergy.system | Active input source | 826 | int16 | 1 | 0 to 32768 | /Ac/ActiveIn/Source | no | 0=Unknown;1=Grid;2=Generator;3=Shore power;240=Not connected | 0 indicates that there is an active input, but it is not configured under Settings → System setup.
com.victronenergy.system | System time in UTC | 830 | uint64 | 1 | 0 to 18446744073709551615 | INTERNAL | no | seconds
com.victronenergy.system | Battery Voltage (System) | 840 | uint16 | 10 | 0 to 6553.5 | /Dc/Battery/Voltage | no | V DC | Battery Voltage determined from different measurements. In order of preference: BMV-voltage (V), Multi-DC-Voltage (CV), MPPT-DC-Voltage (ScV), Charger voltage
com.victronenergy.system | Battery Current (System) | 841 | int16 | 10 | -3276.8 to 3276.7 | /Dc/Battery/Current | no | A DC | Postive: battery begin charged. Negative: battery being discharged
com.victronenergy.system | Battery Power (System) | 842 | int16 | 1 | -32768 to 32767 | /Dc/Battery/Power | no | W | Postive: battery begin charged. Negative: battery being discharged
com.victronenergy.system | Battery State of Charge (System) | 843 | uint16 | 1 | 0 to 100 | /Dc/Battery/Soc | no | % | Best battery state of charge, determined from different measurements.
com.victronenergy.system | Battery state (System) | 844 | uint16 | 1 | 0 to 65536 | /Dc/Battery/State | no | 0=idle;1=charging;2=discharging
com.victronenergy.system | Battery Consumed Amphours (System) | 845 | uint16 | -10 | 0 to -6553.6 | /Dc/Battery/ConsumedAmphours | no | Ah
com.victronenergy.system | Battery Time to Go (System) | 846 | uint16 | 0.01 | 0 to 6553600 | /Dc/Battery/TimeToGo | no | s | Special value: 0 = charging
com.victronenergy.system | PV - DC-coupled power | 850 | uint16 | 1 | 0 to 65536 | /Dc/Pv/Power | no | W | Summation of output power of all connected Solar Chargers
com.victronenergy.system | PV - DC-coupled current | 851 | int16 | 10 | -3276.8 to 3276.7 | /Dc/Pv/Current | no | A DC | Summation of output current of all connected Solar Chargers
com.victronenergy.system | Charger power | 855 | uint16 | 1 | 0 to 65536 | /Dc/Charger/Power | no | W
com.victronenergy.system | DC System Power | 860 | int16 | 1 | -32768 to 32767 | /Dc/System/Power | no | W | Power supplied by Battery to system.
com.victronenergy.system | VE.Bus charge current (System) | 865 | int16 | 10 | -3276.8 to 3276.7 | /Dc/Vebus/Current | no | A DC | Current flowing from the Multi to the dc system. Negative: the other way around.
com.victronenergy.system | VE.Bus charge power (System) | 866 | int16 | 1 | -32768 to 32767 | /Dc/Vebus/Power | no | W | System value etc. AND: Positive: power flowing from the Multi to the dc system. Negative: the other way around.
com.victronenergy.system | RESERVED | 867 | uint16 | 1 | 0 to 65536 |  | no
com.victronenergy.system | Inverter/Charger current | 868 | int32 | 10 | -214748364.8 to 214748364.8 | /Dc/InverterCharger/Current | no
com.victronenergy.system | Inverter/Charger power | 870 | int32 | 1 | -2147483648 to 2147483648 | /Dc/InverterCharger/Power | no
com.victronenergy.system | Power between meter and inverter/charger, L1 | 872 | int32 | 1 | -2147483648 to 2147483648 | /Ac/ConsumptionOnInput/L1/Power | no | W | This is the power shown on the overview in the Loads box
com.victronenergy.system | Power between meter and inverter/charger, L2 | 874 | int32 | 1 | -2147483648 to 2147483648 | /Ac/ConsumptionOnInput/L2/Power | no | W
com.victronenergy.system | Power between meter and inverter/charger, L3 | 876 | int32 | 1 | -2147483648 to 2147483648 | /Ac/ConsumptionOnInput/L3/Power | no | W
com.victronenergy.system | Power on output of inverter/charger, L1 | 878 | int32 | 1 | -2147483648 to 2147483648 | /Ac/ConsumptionOnOutput/L1/Power | no | W
com.victronenergy.system | Power on output of inverter/charger, L2 | 880 | int32 | 1 | -2147483648 to 2147483648 | /Ac/ConsumptionOnOutput/L2/Power | no | W
com.victronenergy.system | Power on output of inverter/charger, L3 | 882 | int32 | 1 | -2147483648 to 2147483648 | /Ac/ConsumptionOnOutput/L3/Power | no | W
com.victronenergy.vebus | Input voltage phase 1 | 3 | uint16 | 10 | 0 to 6553.5 | /Ac/ActiveIn/L1/V | no | V AC
com.victronenergy.vebus | Input voltage phase 2 | 4 | uint16 | 10 | 0 to 6553.5 | /Ac/ActiveIn/L2/V | no | V AC
com.victronenergy.vebus | Input voltage phase 3 | 5 | uint16 | 10 | 0 to 6553.5 | /Ac/ActiveIn/L3/V | no | V AC
com.victronenergy.vebus | Input current phase 1 | 6 | int16 | 10 | -3276.8 to 3276.7 | /Ac/ActiveIn/L1/I | no | A AC | Positive: current flowing from mains to Multi. Negative: current flowing from Multi to mains.
com.victronenergy.vebus | Input current phase 2 | 7 | int16 | 10 | -3276.8 to 3276.7 | /Ac/ActiveIn/L2/I | no | A AC | Positive: current flowing from mains to Multi. Negative: current flowing from Multi to mains.
com.victronenergy.vebus | Input current phase 3 | 8 | int16 | 10 | -3276.8 to 3276.7 | /Ac/ActiveIn/L3/I | no | A AC | Positive: current flowing from mains to Multi. Negative: current flowing from Multi to mains.
com.victronenergy.vebus | Input frequency 1 | 9 | int16 | 100 | -327.68 to 327.67 | /Ac/ActiveIn/L1/F | no | Hz
com.victronenergy.vebus | Input frequency 2 | 10 | int16 | 100 | -327.68 to 327.67 | /Ac/ActiveIn/L2/F | no | Hz
com.victronenergy.vebus | Input frequency 3 | 11 | int16 | 100 | -327.68 to 327.67 | /Ac/ActiveIn/L3/F | no | Hz
com.victronenergy.vebus | Input power 1 | 12 | int16 | 0.1 | -327680 to 327670 | /Ac/ActiveIn/L1/P | no | VA or Watts | Sign meaning equal to Input current
com.victronenergy.vebus | Input power 2 | 13 | int16 | 0.1 | -327680 to 327670 | /Ac/ActiveIn/L2/P | no | VA or Watts | Sign meaning equal to Input current
com.victronenergy.vebus | Input power 3 | 14 | int16 | 0.1 | -327680 to 327670 | /Ac/ActiveIn/L3/P | no | VA or Watts | Sign meaning eaqual to Input current
com.victronenergy.vebus | Output voltage phase 1 | 15 | uint16 | 10 | 0 to 6553.5 | /Ac/Out/L1/V | no | V AC
com.victronenergy.vebus | Output voltage phase 2 | 16 | uint16 | 10 | 0 to 6553.5 | /Ac/Out/L2/V | no | V AC
com.victronenergy.vebus | Output voltage phase 3 | 17 | uint16 | 10 | 0 to 6553.5 | /Ac/Out/L3/V | no | V AC
com.victronenergy.vebus | Output current phase 1 | 18 | int16 | 10 | -3276.8 to 3276.7 | /Ac/Out/L1/I | no | A AC | Postive: current flowing from Multi to the load. Negative: current flowing from load to the Multi.
com.victronenergy.vebus | Output current phase 2 | 19 | int16 | 10 | -3276.8 to 3276.7 | /Ac/Out/L2/I | no | A AC | Postive: current flowing from Multi to the load. Negative: current flowing from load to the Multi.
com.victronenergy.vebus | Output current phase 3 | 20 | int16 | 10 | -3276.8 to 3276.7 | /Ac/Out/L3/I | no | A AC | Postive: current flowing from Multi to the load. Negative: current flowing from load to the Multi.
com.victronenergy.vebus | Output frequency | 21 | int16 | 100 | -327.68 to 327.67 | /Ac/Out/L1/F | no | Hz
com.victronenergy.vebus | Active input current limit | 22 | int16 | 10 | -3276.8 to 3276.7 | /Ac/ActiveIn/CurrentLimit | yes | A | See Venus-OS manual for limitations, for example when VE.Bus BMS or DMC is installed.
com.victronenergy.vebus | Output power 1 | 23 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L1/P | no | VA or Watts | Sign meaning equal to Output current
com.victronenergy.vebus | Output power 2 | 24 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L2/P | no | VA or Watts | Sign meaning equal to Output current
com.victronenergy.vebus | Output power 3 | 25 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L3/P | no | VA or Watts | Sign meaning equal to Output current
com.victronenergy.vebus | Battery voltage | 26 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.vebus | Battery current | 27 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A DC | Positive: current flowing from the Multi to the dc system. Negative: the other way around.
com.victronenergy.vebus | Phase count | 28 | uint16 | 1 | 0 to 65536 | /Ac/NumberOfPhases | no | count
com.victronenergy.vebus | Active input | 29 | uint16 | 1 | 0 to 65536 | /Ac/ActiveIn/ActiveInput | no | 0=AC Input 1;1=AC Input 2;240=Disconnected
com.victronenergy.vebus | VE.Bus state of charge | 30 | uint16 | 10 | 0 to 6553.5 | /Soc | yes | %
com.victronenergy.vebus | VE.Bus state | 31 | uint16 | 1 | 0 to 65536 | /State | no | 0=Off;1=Low Power;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;8=Passthru;9=Inverting;10=Power assist;11=Power supply;244=Sustain;252=External control
com.victronenergy.vebus | VE.Bus Error | 32 | uint16 | 1 | 0 to 65536 | /VebusError | no | 0=No error;1=VE.Bus Error 1: Device is switched off because one of the other phases in the system has switched off;2=VE.Bus Error 2: New and old types MK2 are mixed in the system;3=VE.Bus Error 3: Not all- or more than- the expected devices were found in the system;4=VE.Bus Error 4: No other device whatsoever detected;5=VE.Bus Error 5: Overvoltage on AC-out;6=VE.Bus Error 6: Error in DDC Program;7=VE.Bus BMS connected- which requires an Assistant- but no assistant found;10=VE.Bus Error 10: System time synchronisation problem occurred;14=VE.Bus Error 14: Device cannot transmit data;16=VE.Bus Error 16: Dongle missing;17=VE.Bus Error 17: One of the devices assumed master status because the original master failed;18=VE.Bus Error 18: AC Overvoltage on the output of a slave has occurred while already switched off;22=VE.Bus Error 22: This device cannot function as slave;24=VE.Bus Error 24: Switch-over system protection initiated;25=VE.Bus Error 25: Firmware incompatibility. The firmware of one of the connected device is not sufficiently up to date to operate in conjunction with this device;26=VE.Bus Error 26: Internal error
com.victronenergy.vebus | Switch Position | 33 | uint16 | 1 | 0 to 65536 | /Mode | yes | 1=Charger Only;2=Inverter Only;3=On;4=Off | See Venus-OS manual for limitations, for example when VE.Bus BMS or DMC is installed.
com.victronenergy.vebus | Temperature alarm | 34 | uint16 | 1 | 0 to 65536 | /Alarms/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Low battery alarm | 35 | uint16 | 1 | 0 to 65536 | /Alarms/LowBattery | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Overload alarm | 36 | uint16 | 1 | 0 to 65536 | /Alarms/Overload | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | ESS power setpoint phase 1 | 37 | int16 | 1 | -32768 to 32767 | /Hub4/L1/AcPowerSetpoint | yes | W | ESS Mode 3 - Instructs the multi to charge/discharge with giving power. Negative = discharge. Used by the control loop in grid-parallel systems.
com.victronenergy.vebus | ESS disable charge flag phase | 38 | uint16 | 1 | 0 to 65536 | /Hub4/DisableCharge | yes | 0=Charge allowed;1=Charge disabled | ESS Mode 3 - Enables/Disables charge (0=enabled, 1=disabled). Note that power setpoint will yield to this setting
com.victronenergy.vebus | ESS disable feedback flag phase | 39 | uint16 | 1 | 0 to 65536 | /Hub4/DisableFeedIn | yes | 0=Feed in allowed;1=Feed in disabled | ESS Mode 3 - Enables/Disables feedback (0=enabled, 1=disabled). Note that power setpoint will yield to this setting
com.victronenergy.vebus | ESS power setpoint phase 2 | 40 | int16 | 1 | -32768 to 32767 | /Hub4/L2/AcPowerSetpoint | yes | W | ESS Mode 3 - Instructs the multi to charge/discharge with giving power. Negative = discharge. Used by the control loop in grid-parallel systems.
com.victronenergy.vebus | ESS power setpoint phase 3 | 41 | int16 | 1 | -32768 to 32767 | /Hub4/L3/AcPowerSetpoint | yes | W | ESS Mode 3 - Instructs the multi to charge/discharge with giving power. Negative = discharge. Used by the control loop in grid-parallel systems.
com.victronenergy.vebus | Temperatur sensor alarm | 42 | uint16 | 1 | 0 to 65536 | /Alarms/TemperatureSensor | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Voltage sensor alarm | 43 | uint16 | 1 | 0 to 65535 | /Alarms/VoltageSensor | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Temperature alarm L1 | 44 | uint16 | 1 | 0 to 65535 | /Alarms/L1/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Low battery alarm L1 | 45 | uint16 | 1 | 0 to 65535 | /Alarms/L1/LowBattery | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Overload alarm L1 | 46 | uint16 | 1 | 0 to 65535 | /Alarms/L1/Overload | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Ripple alarm L1 | 47 | uint16 | 1 | 0 to 65535 | /Alarms/L1/Ripple | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Temperature alarm L2 | 48 | uint16 | 1 | 0 to 65535 | /Alarms/L2/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Low battery alarm L2 | 49 | uint16 | 1 | 0 to 65535 | /Alarms/L2/LowBattery | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Overload alarm L2 | 50 | uint16 | 1 | 0 to 65535 | /Alarms/L2/Overload | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Ripple alarm L2 | 51 | uint16 | 1 | 0 to 65535 | /Alarms/L2/Ripple | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Temperature alarm L3 | 52 | uint16 | 1 | 0 to 65535 | /Alarms/L3/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Low battery alarm L3 | 53 | uint16 | 1 | 0 to 65535 | /Alarms/L3/LowBattery | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Overload alarm L3 | 54 | uint16 | 1 | 0 to 65535 | /Alarms/L3/Overload | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Ripple alarm L3 | 55 | uint16 | 1 | 0 to 65535 | /Alarms/L3/Ripple | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus | Disable PV inverter | 56 | uint16 | 1 | 0 to 65535 | /PvInverter/Disable | yes | 0=PV enabled;1=PV disabled | Disable PV inverter on AC out (using frequency shifting). Only works when vebus device is in inverter mode. Needs ESS or PV inverter assistant
com.victronenergy.vebus | VE.Bus BMS allows battery to be charged | 57 | uint16 | 1 | 0 to 65535 | /Bms/AllowToCharge | no | 0=No;1=Yes | VE.Bus BMS allows the battery to be charged
com.victronenergy.vebus | VE.Bus BMS allows battery to be discharged | 58 | uint16 | 1 | 0 to 65535 | /Bms/AllowToDischarge | no | 0=No;1=Yes | VE.Bus BMS allows the battery to be discharged
com.victronenergy.vebus | VE.Bus BMS is expected | 59 | uint16 | 1 | 0 to 65535 | /Bms/BmsExpected | no | 0=No;1=Yes | Presence of VE.Bus BMS is expected based on vebus settings (presence of ESS or BMS assistant)
com.victronenergy.vebus | VE.Bus BMS error | 60 | uint16 | 1 | 0 to 65535 | /Bms/Error | no | 0=No;1=Yes
com.victronenergy.vebus | Battery temperature | 61 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius
com.victronenergy.vebus | VE.Bus Reset | 62 | uint16 | 1 | 0 to 65535 | /SystemReset | yes | 1=VE.Bus reset | Any write action will cause a reset
com.victronenergy.vebus | Phase rotation warning | 63 | uint16 | 1 | 0 to 65535 | /Alarms/PhaseRotation | no | 0=Ok;1=Warning
com.victronenergy.vebus | Grid lost alarm | 64 | uint16 | 1 | 0 to 65535 | /Alarms/GridLost | no | 0=Ok;2=Alarm
com.victronenergy.vebus | Feed DC overvoltage into grid | 65 | uint16 | 1 | 0 to 65535 | /Hub4/DoNotFeedInOvervoltage | yes | 0=Feed in overvoltage;1=Do not feed in overvoltage
com.victronenergy.vebus | Maximum overvoltage feed-in power L1 | 66 | uint16 | 0.01 | 0 to 6553500 | /Hub4/L1/MaxFeedInPower | yes | W
com.victronenergy.vebus | Maximum overvoltage feed-in power L2 | 67 | uint16 | 0.01 | 0 to 6553500 | /Hub4/L2/MaxFeedInPower | yes | W
com.victronenergy.vebus | Maximum overvoltage feed-in power L3 | 68 | uint16 | 0.01 | 0 to 6553500 | /Hub4/L3/MaxFeedInPower | yes | W
com.victronenergy.vebus | AC input 1 ignored | 69 | uint16 | 1 | 0 to 65535 | /Ac/State/IgnoreAcIn1 | no | 0=AC input not ignored;1=AC input ignored
com.victronenergy.vebus | AC input 2 ignored | 70 | uint16 | 1 | 0 to 65535 | /Ac/State/IgnoreAcIn2 | no | 0=AC input not ignored;1=AC input ignored
com.victronenergy.vebus | AcPowerSetpoint acts as feed-in limit | 71 | uint16 | 1 | 0 to 65535 | /Hub4/TargetPowerIsMaxFeedIn | yes | 0=AcPowerSetpoint interpreted normally; 1=AcPowerSetpoint is OvervoltageFeedIn limit | When set to 1, the Multi behaves as if DoNotFeedInOvervoltage is disabled and AcPowerSetpoint is the maximum allowed feed-in
com.victronenergy.vebus | Solar offset voltage | 72 | uint16 | 1 | 0 to 65535 | /Hub4/FixSolarOffsetTo100mV | yes | 0=OvervoltageFeedIn uses 1V offset; 1=OvervoltageFeedIn uses 0.1V offset | When feeding overvoltage into the grid, the solar chargers are set to a higher voltage. This flag determines the size of the offset (per 12V increment).
com.victronenergy.vebus | Sustain active | 73 | uint16 | 1 | 0 to 65535 | /Hub4/Sustain | no | 0=Sustain inactive; 1=Sustain active
com.victronenergy.vebus | Energy from AC-In 1 to AC-out | 74 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcIn1ToAcOut | no | kWh | PLEASE NOTE:
com.victronenergy.vebus | Energy from AC-In 1 to battery | 76 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcIn1ToInverter | no | kWh | Energy counters from the Multi(s) are volatile.
com.victronenergy.vebus | Energy from AC-In 2 to AC-out | 78 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcIn2ToAcOut | no | kWh | These energy counters reset to zero when the Multi is switched off.
com.victronenergy.vebus | Energy from AC-In 2 to battery | 80 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcIn2ToInverter | no | kWh | These energy counters ALSO reset to zero when the GX-device reboots.
com.victronenergy.vebus | Energy from AC-out to AC-in 1 (reverse fed PV) | 82 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcOutToAcIn1 | no | kWh
com.victronenergy.vebus | Energy from AC-out to AC-in 2 (reverse fed PV) | 84 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcOutToAcIn2 | no | kWh
com.victronenergy.vebus | Energy from battery to AC-in 1 | 86 | uint32 | 100 | 0 to 42949672.96 | /Energy/InverterToAcIn1 | no | kWh
com.victronenergy.vebus | Energy from battery to AC-in 2 | 88 | uint32 | 100 | 0 to 42949672.96 | /Energy/InverterToAcIn2 | no | kWh
com.victronenergy.vebus | Energy from battery to AC-out | 90 | uint32 | 100 | 0 to 42949672.96 | /Energy/InverterToAcOut | no | kWh
com.victronenergy.vebus | Energy from AC-out to battery (typically from PV-inverter) | 92 | uint32 | 100 | 0 to 42949672.96 | /Energy/OutToInverter | no | kWh
com.victronenergy.vebus | Low cell voltage imminent | 94 | uint16 | 1 | 0 to 65535 | /Alarms/BmsPreAlarm | no | 0=OK;1=Warning
com.victronenergy.vebus | Charge state | 95 | uint16 | 1 | 0 to 65535 | /VebusChargeState | no | 0=Initialising;1=Bulk;2=Absorption;3=Float;4=Storage;5=Absorb repeat;6=Forced absorb;7=Equalise;8=Bulk stopped;9=Unknown
com.victronenergy.vebus | ESS power setpoint phase 1 | 96 | int32 | 1 | -2147483648 to 2147483648 | /Hub4/L1/AcPowerSetpoint | yes | W | 32-bit compliment to 37, 40 and 41
com.victronenergy.vebus | ESS power setpoint phase 2 | 98 | int32 | 1 | -2147483648 to 2147483648 | /Hub4/L2/AcPowerSetpoint | yes | W
com.victronenergy.vebus | ESS power setpoint phase 3 | 100 | int32 | 1 | -2147483648 to 2147483648 | /Hub4/L3/AcPowerSetpoint | yes | W
com.victronenergy.vebus | Prefer Renewable Energy | 102 | uint16 | 1 | 0 to 65535 | /Dc/0/PreferRenewableEnergy | yes | 0=Renewable energy not preferred;1=Renewable energy preferred | Must be enabled in VE.Configure. This causes the system to charge from the grid at a lower sustain voltage. See manual.
com.victronenergy.vebus | Select Remote Generator | 103 | uint16 | 1 | 0 to 65535 | /Ac/Control/RemoteGeneratorSelected | yes | 0=Generator not selected;1=Generator selected | Informs Multi that a generator is active on AC-in
com.victronenergy.vebus | Remote generator selected | 104 | uint16 | 1 | 0 to 65535 | /Ac/State/RemoteGeneratorSelected | no | 0=Generator not selected;1=Generator selected
com.victronenergy.vebus | Redetect VE.Bus system | 105 | uint16 | 1 | 0 to 65535 | /RedetectSystem | yes | 0=No action;1=Redetect system
com.victronenergy.vebus | Power Assist boost factor | 106 | uint16 | 100 | 0 to 655.35 | /Settings/AssistCurrentBoostFactor | yes |  | These 4 settings were first introduced I Venus 3.30, but immediately redefined as they did not work properly.
com.victronenergy.vebus | Configured output voltage | 107 | uint16 | 100 | 0 to 655.35 | /Settings/InverterOutputVoltage | yes | V AC
com.victronenergy.vebus | PowerAssist enabled | 108 | uint16 | 1 | 0 to 65535 | /Settings/PowerAssistEnabled | yes | 0=Disabled;1=Enabled
com.victronenergy.vebus | UPS function enabled | 109 | uint16 | 1 | 0 to 65535 | /Settings/UpsFunction | yes | 0=Disabled;1=Enabled
com.victronenergy.battery | Battery power | 258 | int16 | 1 | -32768 to 32767 | /Dc/0/Power | no | W
com.victronenergy.battery | Battery voltage | 259 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.battery | Starter battery voltage | 260 | uint16 | 100 | 0 to 655.35 | /Dc/1/Voltage | no | V DC
com.victronenergy.battery | Current | 261 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A DC | Postive: battery begin charged. Negative: battery being discharged
com.victronenergy.battery | Battery temperature | 262 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius | In degrees Celsius
com.victronenergy.battery | Mid-point voltage of the battery bank | 263 | uint16 | 100 | 0 to 655.35 | /Dc/0/MidVoltage | no | V DC
com.victronenergy.battery | Mid-point deviation of the battery bank | 264 | uint16 | 100 | 0 to 655.35 | /Dc/0/MidVoltageDeviation | no | %
com.victronenergy.battery | Consumed Amphours | 265 | uint16 | -10 | 0 to -6553.6 | /ConsumedAmphours | no | Ah | Always negative (to have the same sign as the current).
com.victronenergy.battery | State of charge | 266 | uint16 | 10 | 0 to 6553.6 | /Soc | no | %
com.victronenergy.battery | Alarm | 267 | uint16 | 1 | 0 to 65535 | /Alarms/Alarm | no | 0=No alarm;2=Alarm | 2015-01-19: Deprecated for CCGX. Value is always 0.
com.victronenergy.battery | Low voltage alarm | 268 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=No alarm;2=Alarm
com.victronenergy.battery | High voltage alarm | 269 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Low starter-voltage alarm | 270 | uint16 | 1 | 0 to 65535 | /Alarms/LowStarterVoltage | no | 0=No alarm;2=Alarm
com.victronenergy.battery | High starter-voltage alarm | 271 | uint16 | 1 | 0 to 65535 | /Alarms/HighStarterVoltage | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Low State-of-charge alarm | 272 | uint16 | 1 | 0 to 65535 | /Alarms/LowSoc | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Low temperature alarm | 273 | uint16 | 1 | 0 to 65535 | /Alarms/LowTemperature | no | 0=No alarm;2=Alarm
com.victronenergy.battery | High temperature alarm | 274 | uint16 | 1 | 0 to 65535 | /Alarms/HighTemperature | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Mid-voltage alarm | 275 | uint16 | 1 | 0 to 65535 | /Alarms/MidVoltage | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Low fused-voltage alarm | 276 | uint16 | 1 | 0 to 65535 | /Alarms/LowFusedVoltage | no | 0=No alarm;2=Alarm | 2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery | High fused-voltage alarm | 277 | uint16 | 1 | 0 to 65535 | /Alarms/HighFusedVoltage | no | 0=No alarm;2=Alarm | 2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery | Fuse blown alarm | 278 | uint16 | 1 | 0 to 65535 | /Alarms/FuseBlown | no | 0=No alarm;2=Alarm
com.victronenergy.battery | High internal-temperature alarm | 279 | uint16 | 1 | 0 to 65535 | /Alarms/HighInternalTemperature | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Relay status | 280 | uint16 | 1 | 0 to 65535 | /Relay/0/State | yes | 0=Open;1=Closed | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Deepest discharge | 281 | uint16 | -10 | 0 to -6553.6 | /History/DeepestDischarge | no | Ah | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Last discharge | 282 | uint16 | -10 | 0 to -6553.6 | /History/LastDischarge | no | Ah | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Average discharge | 283 | uint16 | -10 | 0 to -6553.6 | /History/AverageDischarge | no | Ah | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Charge cycles | 284 | uint16 | 1 | 0 to 65535 | /History/ChargeCycles | no | count | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Full discharges | 285 | uint16 | 1 | 0 to 65535 | /History/FullDischarges | no | count | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Total Ah drawn | 286 | uint16 | -10 | 0 to -6553.6 | /History/TotalAhDrawn | no | Ah | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Minimum voltage | 287 | uint16 | 100 | 0 to 655.35 | /History/MinimumVoltage | no | V DC | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Maximum voltage | 288 | uint16 | 100 | 0 to 655.35 | /History/MaximumVoltage | no | V DC | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Time since last full charge | 289 | uint16 | 0.01 | 0 to 6553500 | /History/TimeSinceLastFullCharge | no | seconds | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Automatic syncs | 290 | uint16 | 1 | 0 to 65535 | /History/AutomaticSyncs | no | count | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Low voltage alarms | 291 | uint16 | 1 | 0 to 65535 | /History/LowVoltageAlarms | no | count | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | High voltage alarms | 292 | uint16 | 1 | 0 to 65535 | /History/HighVoltageAlarms | no | count | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Low starter voltage alarms | 293 | uint16 | 1 | 0 to 65535 | /History/LowStarterVoltageAlarms | no | count | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | High starter voltage alarms | 294 | uint16 | 1 | 0 to 65535 | /History/HighStarterVoltageAlarms | no | count | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Minimum starter voltage | 295 | uint16 | 100 | 0 to 655.35 | /History/MinimumStarterVoltage | no | V DC | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Maximum starter voltage | 296 | uint16 | 100 | 0 to 655.35 | /History/MaximumStarterVoltage | no | V DC | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Low fused-voltage alarms | 297 | uint16 | 1 | 0 to 65535 | /History/LowFusedVoltageAlarms | no | count | 2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery | High fused-voltage alarms | 298 | uint16 | 1 | 0 to 65535 | /History/HighFusedVoltageAlarms | no | count | 2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery | Minimum fused voltage | 299 | uint16 | 100 | 0 to 655.35 | /History/MinimumFusedVoltage | no | V DC | 2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery | Maximum fused voltage | 300 | uint16 | 100 | 0 to 655.35 | /History/MaximumFusedVoltage | no | V DC | 2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery | Discharged Energy | 301 | uint16 | 10 | 0 to 6553.5 | /History/DischargedEnergy | no | kWh | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Charged Energy | 302 | uint16 | 10 | 0 to 6553.5 | /History/ChargedEnergy | no | kWh | Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | Time to go | 303 | uint16 | 0.01 | 0 to 6553500 | /TimeToGo | no | seconds | Special value: 0 = charging. Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery | State of health | 304 | uint16 | 10 | 0 to 6553.5 | /Soh | no | % | Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery | Max charge voltage | 305 | uint16 | 10 | 0 to 6553.5 | /Info/MaxChargeVoltage | no | V DC | Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery | Min discharge voltage | 306 | uint16 | 10 | 0 to 6553.5 | /Info/BatteryLowVoltage | no | V DC | Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery | Max charge current | 307 | uint16 | 10 | 0 to 6553.5 | /Info/MaxChargeCurrent | no | A DC | Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery | Max discharge current | 308 | uint16 | 10 | 0 to 6553.5 | /Info/MaxDischargeCurrent | no | A DC | Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery | Capacity | 309 | uint16 | 10 | 0 to 6553.5 | /Capacity | no | Ah
com.victronenergy.battery | Diagnostics; 1st last error timestamp | 310 | int32 | 1 | -2147483648 to 2147483648 | /Diagnostics/LastErrors/1/Time | no
com.victronenergy.battery | Diagnostics; 2nd last error timestamp | 312 | int32 | 1 | -2147483648 to 2147483648 | /Diagnostics/LastErrors/2/Time | no
com.victronenergy.battery | Diagnostics; 3rd last error timestamp | 314 | int32 | 1 | -2147483648 to 2147483648 | /Diagnostics/LastErrors/3/Time | no
com.victronenergy.battery | Diagnostics; 4th last error timestamp | 316 | int32 | 1 | -2147483648 to 2147483648 | /Diagnostics/LastErrors/4/Time | no
com.victronenergy.battery | Minimum cell temperature | 318 | int16 | 10 | -3276.8 to 3276.7 | /System/MinCellTemperature | no | Degrees celsius
com.victronenergy.battery | Maximum cell temperature | 319 | int16 | 10 | -3276.8 to 3276.7 | /System/MaxCellTemperature | no | Degrees celsius
com.victronenergy.battery | High charge current alarm | 320 | uint16 | 1 | 0 to 65535 | /Alarms/HighChargeCurrent | no | 0=No alarm;2=Alarm
com.victronenergy.battery | High discharge current alarm | 321 | uint16 | 1 | 0 to 65535 | /Alarms/HighDischargeCurrent | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Cell imbalance alarm | 322 | uint16 | 1 | 0 to 65535 | /Alarms/CellImbalance | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Internal failure alarm | 323 | uint16 | 1 | 0 to 65535 | /Alarms/InternalFailure | no | 0=No alarm;2=Alarm
com.victronenergy.battery | High charge temperature alarm | 324 | uint16 | 1 | 0 to 65535 | /Alarms/HighChargeTemperature | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Low charge temperature alarm | 325 | uint16 | 1 | 0 to 65535 | /Alarms/LowChargeTemperature | no | 0=No alarm;2=Alarm
com.victronenergy.battery | Low cell voltage alarm | 326 | uint16 | 1 | 0 to 65535 | /Alarms/LowCellVoltage | no | 0=No alarm;1=Almost discharged;2=Alarm
com.victronenergy.battery | Mode | 327 | uint16 | 1 | 0 to 65535 | /Mode | yes | 0=Open;14=Standby
com.victronenergy.solarcharger | Battery voltage | 771 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.solarcharger | Battery current | 772 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A DC
com.victronenergy.solarcharger | Battery temperature | 773 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius | VE.Can MPPTs only
com.victronenergy.solarcharger | Charger on/off | 774 | uint16 | 1 | 0 to 65535 | /Mode | yes | 1=On;4=Off | VE.Can MPPTs only
com.victronenergy.solarcharger | Charge state | 775 | uint16 | 1 | 0 to 65535 | /State | no | 0=Off;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;11=Other (Hub-1);252=External control
com.victronenergy.solarcharger | PV voltage | 776 | uint16 | 100 | 0 to 655.35 | /Pv/V | no | V DC | Not available if multiple VE.Can chargers are combined
com.victronenergy.solarcharger | PV current | 777 | int16 | 10 | -3276.8 to 3276.7 |  | no | A DC | Calculated from /Yield/Power and /Pv/V
com.victronenergy.solarcharger | Equalization pending | 778 | uint16 | 1 | 0 to 65535 | /Equalization/Pending | no | 0=No;1=Yes;2=Error;3=Unavailable- Unknown
com.victronenergy.solarcharger | Equalization time remaining | 779 | uint16 | 10 | 0 to 6553.5 | /Equalization/TimeRemaining | no | seconds
com.victronenergy.solarcharger | Relay on the charger | 780 | uint16 | 1 | 0 to 65535 | /Relay/0/State | no | 0=Open;1=Closed
com.victronenergy.solarcharger |  | 781 | uint16 | 1 | 0 to 65535 | /Alarms/Alarm | no | 0=No alarm;2=Alarm | Deprecated. Value is always 0
com.victronenergy.solarcharger | Low batt. voltage alarm | 782 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=No alarm;2=Alarm
com.victronenergy.solarcharger | High batt. voltage alarm | 783 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=No alarm;2=Alarm
com.victronenergy.solarcharger | Yield today | 784 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Yield | no | kWh | Today's yield
com.victronenergy.solarcharger | Maximum charge power today | 785 | uint16 | 1 | 0 to 65535 | /History/Daily/0/MaxPower | no | W | Today's maximum power
com.victronenergy.solarcharger | Yield yesterday | 786 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Yield | no | kWh | Yesterday's yield
com.victronenergy.solarcharger | Maximum charge power yesterday | 787 | uint16 | 1 | 0 to 65535 | /History/Daily/1/MaxPower | no | W | Yesterday's maximum power
com.victronenergy.solarcharger | Error code | 788 | uint16 | 1 | 0 to 65535 | /ErrorCode | no | 0=No error;1=Battery temperature too high;2=Battery voltage too high;3=Battery temperature sensor miswired (+);4=Battery temperature sensor miswired (-);5=Battery temperature sensor disconnected;6=Battery voltage sense miswired (+);7=Battery voltage sense miswired (-);8=Battery voltage sense disconnected;9=Battery voltage wire losses too high;17=Charger temperature too high;18=Charger over-current;19=Charger current polarity reversed;20=Bulk time limit reached;22=Charger temperature sensor miswired;23=Charger temperature sensor disconnected;34=Input current too high
com.victronenergy.solarcharger | PV power | 789 | uint16 | 10 | 0 to 6553.5 | /Yield/Power | no | W
com.victronenergy.solarcharger | User yield | 790 | uint16 | 10 | 0 to 6553.5 | /Yield/User | no | kWh | Energy generated by the solarcharger since last user reset
com.victronenergy.solarcharger | MPP operation mode | 791 | uint16 | 1 | 0 to 65535 | /MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.solarcharger | PV voltage for tracker 0 | 3700 | uint16 | 100 | 0 to 655.35 | /Pv/0/V | no | V DC
com.victronenergy.solarcharger | PV voltage for tracker 1 | 3701 | uint16 | 100 | 0 to 655.35 | /Pv/1/V | no | V DC
com.victronenergy.solarcharger | PV voltage for tracker 2 | 3702 | uint16 | 100 | 0 to 655.35 | /Pv/2/V | no | V DC
com.victronenergy.solarcharger | PV voltage for tracker 3 | 3703 | uint16 | 100 | 0 to 655.35 | /Pv/3/V | no | V DC
com.victronenergy.solarcharger | RESERVED | 3704 | uint16 | 1 | 0 to 65535 |  | no
com.victronenergy.solarcharger | RESERVED | 3705 | uint16 | 1 | 0 to 65535 |  | no
com.victronenergy.solarcharger | RESERVED | 3706 | uint16 | 1 | 0 to 65535 |  | no
com.victronenergy.solarcharger | RESERVED | 3707 | uint16 | 1 | 0 to 65535 |  | no
com.victronenergy.solarcharger | Yield today for tracker 0 | 3708 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/0/Yield | no | kWh
com.victronenergy.solarcharger | Yield today for tracker 1 | 3709 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/1/Yield | no | kWh
com.victronenergy.solarcharger | Yield today for tracker 2 | 3710 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/2/Yield | no | kWh
com.victronenergy.solarcharger | Yield today for tracker 3 | 3711 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/3/Yield | no | kWh
com.victronenergy.solarcharger | Yield yesterday for tracker 0 | 3712 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/0/Yield | no | kWh
com.victronenergy.solarcharger | Yield yesterday for tracker 1 | 3713 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/1/Yield | no | kWh
com.victronenergy.solarcharger | Yield yesterday for tracker 2 | 3714 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/2/Yield | no | kWh
com.victronenergy.solarcharger | Yield yesterday for tracker 3 | 3715 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/3/Yield | no | kWh
com.victronenergy.solarcharger | Maximum charge power today for tracker 0 | 3716 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/0/MaxPower | no | W
com.victronenergy.solarcharger | Maximum charge power today for tracker 1 | 3717 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/1/MaxPower | no | W
com.victronenergy.solarcharger | Maximum charge power today for tracker 2 | 3718 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/2/MaxPower | no | W
com.victronenergy.solarcharger | Maximum charge power today for tracker 3 | 3719 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/3/MaxPower | no | W
com.victronenergy.solarcharger | Maximum charge power yesterday tracker 0 | 3720 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/0/MaxPower | no | W
com.victronenergy.solarcharger | Maximum charge power yesterday tracker 1 | 3721 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/1/MaxPower | no | W
com.victronenergy.solarcharger | Maximum charge power yesterday tracker 2 | 3722 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/2/MaxPower | no | W
com.victronenergy.solarcharger | Maximum charge power yesterday tracker 3 | 3723 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/3/MaxPower | no | W
com.victronenergy.solarcharger | PV power for tracker 0 | 3724 | uint16 | 1 | 0 to 65535 | /Pv/0/P | no | W
com.victronenergy.solarcharger | PV power for tracker 1 | 3725 | uint16 | 1 | 0 to 65535 | /Pv/1/P | no | W
com.victronenergy.solarcharger | PV power for tracker 2 | 3726 | uint16 | 1 | 0 to 65535 | /Pv/2/P | no | W
com.victronenergy.solarcharger | PV power for tracker 3 | 3727 | uint16 | 1 | 0 to 65535 | /Pv/3/P | no | W
com.victronenergy.solarcharger | User yield | 3728 | uint32 | 1 | 0 to 4294967295 | /Yield/User | no | kWh | Energy generated by the solarcharger since last user reset
com.victronenergy.solarcharger | PV power | 3730 | uint16 | 1 | 0 to 65535 | /Yield/Power | no | W
com.victronenergy.solarcharger | MPP operation mode tracker 1 | 3731 | uint16 | 1 | 0 to 65535 | /Pv/0/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.solarcharger | MPP operation mode tracker 2 | 3732 | uint16 | 1 | 0 to 65535 | /Pv/1/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.solarcharger | MPP operation mode tracker 3 | 3733 | uint16 | 1 | 0 to 65535 | /Pv/2/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.solarcharger | MPP operation mode tracker 4 | 3734 | uint16 | 1 | 0 to 65535 | /Pv/3/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.pvinverter | Position | 1026 | uint16 | 1 | 0 to 65535 | /Position | no | 0=AC input 1;1=AC output;2=AC input 2
com.victronenergy.pvinverter | L1 Voltage | 1027 | uint16 | 10 | 0 to 6553.5 | /Ac/L1/Voltage | no | V AC
com.victronenergy.pvinverter | L1 Current | 1028 | int16 | 10 | -3276.8 to 3276.7 | /Ac/L1/Current | no | A AC
com.victronenergy.pvinverter | L1 Power | 1029 | uint16 | 1 | 0 to 65535 | /Ac/L1/Power | no | W
com.victronenergy.pvinverter | L1 Energy | 1030 | uint16 | 100 | 0 to 655.35 | /Ac/L1/Energy/Forward | no | kWh | Deprecated. Use 1046 instead.
com.victronenergy.pvinverter | L2 Voltage | 1031 | uint16 | 10 | 0 to 6553.5 | /Ac/L2/Voltage | no | V AC
com.victronenergy.pvinverter | L2 Current | 1032 | int16 | 10 | -3276.8 to 3276.7 | /Ac/L2/Current | no | A AC
com.victronenergy.pvinverter | L2 Power | 1033 | uint16 | 1 | 0 to 65535 | /Ac/L2/Power | no | W
com.victronenergy.pvinverter | L2 Energy | 1034 | uint16 | 100 | 0 to 655.35 | /Ac/L2/Energy/Forward | no | kWh | Deprecated. Use 1048 instead.
com.victronenergy.pvinverter | L3 Voltage | 1035 | uint16 | 10 | 0 to 6553.5 | /Ac/L3/Voltage | no | V AC
com.victronenergy.pvinverter | L3 Current | 1036 | int16 | 10 | -3276.8 to 3276.7 | /Ac/L3/Current | no | A AC
com.victronenergy.pvinverter | L3 Power | 1037 | uint16 | 1 | 0 to 65535 | /Ac/L3/Power | no | W
com.victronenergy.pvinverter | L3 Energy | 1038 | uint16 | 100 | 0 to 655.35 | /Ac/L3/Energy/Forward | no | kWh | Deprecated. Use 1050 instead.
com.victronenergy.pvinverter | Serial | 1039 | string[7] | 1 | Max 14 characters | /Serial | no |  | The system serial as string (MSB of first register: first character, LSB of last register: last character).
com.victronenergy.pvinverter | L1 Energy | 1046 | uint32 | 100 | 0 to 42949672.96 | /Ac/L1/Energy/Forward | no | kWh
com.victronenergy.pvinverter | L2 Energy | 1048 | uint32 | 100 | 0 to 42949672.96 | /Ac/L2/Energy/Forward | no | kWh
com.victronenergy.pvinverter | L3 Energy | 1050 | uint32 | 100 | 0 to 42949672.96 | /Ac/L3/Energy/Forward | no | kWh
com.victronenergy.pvinverter | Total Power | 1052 | int32 | 1 | - 2147483648 to 2147483647 | /Ac/Power | no | W
com.victronenergy.pvinverter | Maximum Power Capacity | 1054 | uint32 | 1 | 0 to 4294967295 | /Ac/MaxPower | no | W
com.victronenergy.pvinverter | Power limit | 1056 | uint32 | 1 | 0 to 4294967295 | /Ac/PowerLimit | yes | W | For use in ESS mode 3
com.victronenergy.pvinverter | L1 Power | 1058 | uint32 | 1 | 0 to 4294967295 | /Ac/L1/Power | no | W
com.victronenergy.pvinverter | L2 Power | 1060 | uint32 | 1 | 0 to 4294967295 | /Ac/L2/Power | no | W
com.victronenergy.pvinverter | L3 Power | 1062 | uint32 | 1 | 0 to 4294967295 | /Ac/L3/Power | no | W
com.victronenergy.battery | State | 1282 | uint16 | 1 | 0 to 65535 | /State | no | 0=Initializing (Wait start);1=Initializing (before boot);2=Initializing (Before boot delay);3=Initializing (Wait boot);4=Initializing;5=Initializing (Measure battery voltage);6=Initializing (Calculate battery voltage);7=Initializing (Wait bus voltage);8=Initializing (Wait for lynx shunt);9=Running;10=Error (10);11=Unused (11);12=Shutdown;13=Slave updating;14=Standby;15=Going to run;16=Pre-charging;17=Contactor check
com.victronenergy.battery | Error | 1283 | uint16 | 1 | 0 to 65535 | /ErrorCode | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
com.victronenergy.battery | System-switch | 1284 | uint16 | 1 | 0 to 65535 | /SystemSwitch | no | 0=Disabled;1=Enabled
com.victronenergy.battery | Balancing | 1285 | uint16 | 1 | 0 to 65535 | /Balancing | no | 0=Inactive;1=Active
com.victronenergy.battery | System; number of batteries | 1286 | uint16 | 1 | 0 to 65535 | /System/NrOfBatteries | no | count
com.victronenergy.battery | System; batteries parallel | 1287 | uint16 | 1 | 0 to 65535 | /System/BatteriesParallel | no | count
com.victronenergy.battery | System; batteries series | 1288 | uint16 | 1 | 0 to 65535 | /System/BatteriesSeries | no | count
com.victronenergy.battery | System; number of cells per battery | 1289 | uint16 | 1 | 0 to 65535 | /System/NrOfCellsPerBattery | no | count
com.victronenergy.battery | System; minimum cell voltage | 1290 | uint16 | 100 | 0 to 655.35 | /System/MinCellVoltage | no | V DC
com.victronenergy.battery | System; maximum cell voltage | 1291 | uint16 | 100 | 0 to 655.35 | /System/MaxCellVoltage | no | V DC
com.victronenergy.battery | Diagnostics; shutdowns due to error | 1292 | uint16 | 1 | 0 to 65535 | /Diagnostics/ShutDownsDueError | no | count
com.victronenergy.battery | Diagnostics; 1st last error | 1293 | uint16 | 1 | 0 to 65535 | /Diagnostics/LastErrors/1/Error | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
com.victronenergy.battery | Diagnostics; 2nd last error | 1294 | uint16 | 1 | 0 to 65535 | /Diagnostics/LastErrors/2/Error | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
com.victronenergy.battery | Diagnostics; 3rd last error | 1295 | uint16 | 1 | 0 to 65535 | /Diagnostics/LastErrors/3/Error | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
com.victronenergy.battery | Diagnostics; 4th last error | 1296 | uint16 | 1 | 0 to 65535 | /Diagnostics/LastErrors/4/Error | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
com.victronenergy.battery | IO; allow to charge | 1297 | uint16 | 1 | 0 to 65535 | /Io/AllowToCharge | no | 0=No;1=Yes
com.victronenergy.battery | IO; allow to discharge | 1298 | uint16 | 1 | 0 to 65535 | /Io/AllowToDischarge | no | 0=No;1=Yes
com.victronenergy.battery | IO; external relay | 1299 | uint16 | 1 | 0 to 65535 | /Io/ExternalRelay | no | 0=Inactive;1=Active
com.victronenergy.battery | History; Min cell-voltage | 1300 | uint16 | 100 | 0 to 655.35 | /History/MinimumCellVoltage | no | V DC
com.victronenergy.battery | History; Max cell-voltage | 1301 | uint16 | 100 | 0 to 655.35 | /History/MaximumCellVoltage | no | V DC
com.victronenergy.battery | System; number of modules offline | 1302 | uint16 | 1 | 0 to 65535 | /System/NrOfModulesOffline | no
com.victronenergy.battery | System; number of modules online | 1303 | uint16 | 1 | 0 to 65535 | /System/NrOfModulesOnline | no
com.victronenergy.battery | System; number of modules blocking charge | 1304 | uint16 | 1 | 0 to 65535 | /System/NrOfModulesBlockingCharge | no
com.victronenergy.battery | System; number of modules blocking discharge | 1305 | uint16 | 1 | 0 to 65535 | /System/NrOfModulesBlockingDischarge | no
com.victronenergy.battery | System; ID of module with lowest cell voltage | 1306 | string[4] |  |  | /System/MinVoltageCellId | no
com.victronenergy.battery | System; ID of module with highest cell voltage | 1310 | string[4] |  |  | /System/MaxVoltageCellId | no
com.victronenergy.battery | System; ID of module with lowest cell temperature | 1314 | string[4] |  |  | /System/MinTemperatureCellId | no
com.victronenergy.battery | System; ID of module with highest cell temperature | 1318 | string[4] |  |  | /System/MaxTemperatureCellId | no
com.victronenergy.battery | Mode | 1319 | uint16 | 1 | 0 to 65535 | /Mode | yes | 3=On;252=Standby
com.victronenergy.battery | Balancer status | 1320 | uint16 | 1 | 0 to 65535 | /Balancer/Status | no | 0=Unknown;1=Balanced;2=Balancing;3=Cell imbalance
com.victronenergy.battery | SmartLithium error flag: Communication | 1321 | uint16 | 1 | 0 to 65535 | /Errors/SmartLithium/Communication | no
com.victronenergy.battery | SmartLithium error flag: Voltage | 1322 | uint16 | 1 | 0 to 65535 | /Errors/SmartLithium/Voltage | no
com.victronenergy.battery | SmartLithium error flag: Battery number | 1323 | uint16 | 1 | 0 to 65535 | /Errors/SmartLithium/NrOfBatteries | no
com.victronenergy.battery | SmartLithium error flag: Invalid configuration | 1324 | uint16 | 1 | 0 to 65535 | /Errors/SmartLithium/InvalidConfiguration | no
com.victronenergy.battery | RESERVED | 1325 | uint16
com.victronenergy.battery | RESERVED | 1326 | uint16
com.victronenergy.battery | RESERVED | 1327 | uint16
com.victronenergy.battery | Connection information | 1328 | string[8] |  |  | /ConnectionInformation | no |  | Information from a managed battery about alternate connection information, such as a URL or IP address.
com.victronenergy.motordrive | Motor RPM | 2048 | int16 | 1 | -32768 to 32767 | /Motor/RPM | no | RPM
com.victronenergy.motordrive | Motor temperature | 2049 | int16 | 10 | -3276.8 to 3276.7 | /Motor/Temperature | no | Degrees celsius
com.victronenergy.motordrive | Controller DC Voltage | 2050 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.motordrive | Controller DC Current | 2051 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A DC
com.victronenergy.motordrive | Controller DC Power | 2052 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Power | no | W | Positive = being powered from battery, Negative is charging battery (regeneration)
com.victronenergy.motordrive | Controller Temperature | 2053 | int16 | 10 | -3276.8 to 3276.7 | /Controller/Temperature | no | Degrees celsius
com.victronenergy.charger | Output 1 - voltage | 2307 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.charger | Output 1 - current | 2308 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A DC
com.victronenergy.charger | Output 1 - temperature | 2309 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius
com.victronenergy.charger | Output 2 - voltage | 2310 | uint16 | 100 | 0 to 655.35 | /Dc/1/Voltage | no | V DC
com.victronenergy.charger | Output 2 - current | 2311 | int16 | 10 | -3276.8 to 3276.7 | /Dc/1/Current | no | A DC
com.victronenergy.charger | Output 3 - voltage | 2312 | uint16 | 100 | 0 to 655.35 | /Dc/2/Voltage | no | V DC
com.victronenergy.charger | Output 3 - current | 2313 | int16 | 10 | -3276.8 to 3276.7 | /Dc/2/Current | no | A DC
com.victronenergy.charger | AC Current | 2314 | int16 | 10 | -3276.8 to 3276.7 | /Ac/In/L1/I | no | A AC
com.victronenergy.charger | AC Power | 2315 | uint16 | 1 | 0 to 65535 | /Ac/In/L1/P | no | W DC
com.victronenergy.charger | AC Current limit | 2316 | int16 | 10 | -3276.8 to 3276.7 | /Ac/In/CurrentLimit | yes | A AC
com.victronenergy.charger | Charger on/off | 2317 | uint16 | 1 | 0 to 65535 | /Mode | yes | 0=Off;1=On;2=Error;3=Unavailable- Unknown
com.victronenergy.charger | Charge state | 2318 | uint16 | 1 | 0 to 65535 | /State | no | 0=Off;1=Low Power Mode;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;8=Passthru;9=Inverting;10=Power assist;11=Power supply mode;252=External control
com.victronenergy.charger | Error code | 2319 | uint16 | 1 | 0 to 65535 | /ErrorCode | no | 0=No error;1=Battery temperature too high;2=Battery voltage too high;3=Battery temperature sensor miswired (+);4=Battery temperature sensor miswired (-);5=Battery temperature sensor disconnected;6=Battery voltage sense miswired (+);7=Battery voltage sense miswired (-);8=Battery voltage sense disconnected;9=Battery voltage wire losses too high;17=Charger temperature too high;18=Charger over-current;19=Charger current polarity reversed;20=Bulk time limit reached;22=Charger temperature sensor miswired;23=Charger temperature sensor disconnected;34=Input current too high
com.victronenergy.charger | Relay on the charger | 2320 | uint16 | 1 | 0 to 65535 | /Relay/0/State | no | 0=Open;1=Closed
com.victronenergy.charger | Low voltage alarm | 2321 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=No alarm;2=Alarm
com.victronenergy.charger | High voltage alarm | 2322 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=No alarm;2=Alarm
com.victronenergy.grid | Grid L1 - Power | 2600 | int16 | 1 | -32768 to 32767 | /Ac/L1/Power | no | W
com.victronenergy.grid | Grid L2 - Power | 2601 | int16 | 1 | -32768 to 32767 | /Ac/L2/Power | no | W
com.victronenergy.grid | Grid L3 - Power | 2602 | int16 | 1 | -32768 to 32767 | /Ac/L3/Power | no | W
com.victronenergy.grid | Grid L1 - Energy from net | 2603 | uint16 | 100 | 0 to 655.35 | /Ac/L1/Energy/Forward | no | kWh
com.victronenergy.grid | Grid L2 - Energy from net | 2604 | uint16 | 100 | 0 to 655.35 | /Ac/L2/Energy/Forward | no | kWh
com.victronenergy.grid | Grid L3 - Energy from net | 2605 | uint16 | 100 | 0 to 655.35 | /Ac/L3/Energy/Forward | no | kWh
com.victronenergy.grid | Grid L1 - Energy to net | 2606 | uint16 | 100 | 0 to 655.35 | /Ac/L1/Energy/Reverse | no | kWh
com.victronenergy.grid | Grid L2 - Energy to net | 2607 | uint16 | 100 | 0 to 655.35 | /Ac/L2/Energy/Reverse | no | kWh
com.victronenergy.grid | Grid L3 - Energy to net | 2608 | uint16 | 100 | 0 to 655.35 | /Ac/L3/Energy/Reverse | no | kWh
com.victronenergy.grid | Serial | 2609 | string[7] |  | 14 characters | /Serial | no |  | The grid meter serial as string (MSB of first register: first character, LSB of last register: last character).
com.victronenergy.grid | Grid L1 – Voltage | 2616 | uint16 | 10 | 0 to 6553.5 | /Ac/L1/Voltage | no | V AC
com.victronenergy.grid | Grid L1 – Current | 2617 | int16 | 10 | -3276.8 to 3276.7 | /Ac/L1/Current | no | A AC
com.victronenergy.grid | Grid L2 – Voltage | 2618 | uint16 | 10 | 0 to 6553.5 | /Ac/L2/Voltage | no | V AC
com.victronenergy.grid | Grid L2 – Current | 2619 | int16 | 10 | -3276.8 to 3276.7 | /Ac/L2/Current | no | A AC
com.victronenergy.grid | Grid L3 – Voltage | 2620 | uint16 | 10 | 0 to 6553.5 | /Ac/L3/Voltage | no | V AC
com.victronenergy.grid | Grid L3 – Current | 2621 | int16 | 10 | -3276.8 to 3276.7 | /Ac/L3/Current | no | A AC
com.victronenergy.grid | Grid L1 - Energy from net | 2622 | uint32 | 100 | 0 to 42949672.96 | /Ac/L1/Energy/Forward | no | kWh
com.victronenergy.grid | Grid L2 - Energy from net | 2624 | uint32 | 100 | 0 to 42949672.96 | /Ac/L2/Energy/Forward | no | kWh
com.victronenergy.grid | Grid L3 - Energy from net | 2626 | uint32 | 100 | 0 to 42949672.96 | /Ac/L3/Energy/Forward | no | kWh
com.victronenergy.grid | Grid L1 - Energy to net | 2628 | uint32 | 100 | 0 to 42949672.96 | /Ac/L1/Energy/Reverse | no | kWh
com.victronenergy.grid | Grid L2 - Energy to net | 2630 | uint32 | 100 | 0 to 42949672.96 | /Ac/L2/Energy/Reverse | no | kWh
com.victronenergy.grid | Grid L3 - Energy to net | 2632 | uint32 | 100 | 0 to 42949672.96 | /Ac/L3/Energy/Reverse | no | kWh
com.victronenergy.grid | Total Energy from net | 2634 | uint32 | 100 | 0 to 42949672.96 | /Ac/Energy/Forward | no | kWh | Depending on the energy summation method used by the meter, this may be different to the sum of the individual counters
com.victronenergy.grid | Total Energy to net | 2636 | uint32 | 100 | 0 to 42949672.96 | /Ac/Energy/Reverse | no | kWh
com.victronenergy.grid | Grid L1 - Power | 2638 | int32 | 1 | -2147483648 to 2147483648 | /Ac/L1/Power | no | W
com.victronenergy.grid | Grid L2 - Power | 2640 | int32 | 1 | -2147483648 to 2147483648 | /Ac/L2/Power | no | W
com.victronenergy.grid | Grid L3 - Power | 2642 | int32 | 1 | -2147483648 to 2147483648 | /Ac/L3/Power | no | W
com.victronenergy.settings | ESS control loop setpoint | 2700 | int16 | 1 | -32768 to 32767 | /Settings/Cgwacs/AcPowerSetPoint | yes | W | ESS Mode 2 - Setpoint for the ESS control-loop in the CCGX. The control-loop will increase/decrease the Multi charge/discharge power to get the grid reading to this setpoint
com.victronenergy.settings | ESS max charge current (fractional) | 2701 | uint16 | 1 | 0 to 100 | /Settings/Cgwacs/MaxChargePercentage | yes | % | ESS Mode 2 - Max charge current for ESS control-loop. The control-loop will use this value to limit the multi power setpoint. For DVCC, use 2705 instead.
com.victronenergy.settings | ESS max discharge current (fractional) | 2702 | uint16 | 1 | 0 to 100 | /Settings/Cgwacs/MaxDischargePercentage | yes | % | ESS Mode 2 - Max discharge current for ESS control-loop. The control-loop will use this value to limit the multi power setpoint. Currently a value < 50% will disable discharge completely. >=50% allows. Consider using 2704 instead.
com.victronenergy.settings | ESS control loop setpoint | 2703 | int16 | 0.01 | -3276800 to 3276700 | /Settings/Cgwacs/AcPowerSetPoint | yes | W | ESS Mode 2 – Same as 2700, but with a different scale factor. Meant for values larger than +-32kW.
com.victronenergy.settings | ESS max discharge current | 2704 | int16 | 0.1 | -327680 to 327670 | /Settings/Cgwacs/MaxDischargePower | yes | W | ESS Mode 2 – similar to 2702, but as an absolute value instead of a percentage.
com.victronenergy.settings | DVCC system max charge current | 2705 | int16 | 1 | -32768 to 32767 | /Settings/SystemSetup/MaxChargeCurrent | yes | A DC | ESS Mode 2 with DVCC – Maximum system charge current. -1 Disables.
com.victronenergy.settings | Maximum System Grid Feed In | 2706 | int16 | 0.01 | -3276800 to 3276700 | /Settings/Cgwacs/MaxFeedInPower | yes | W | -1: No limit, >=0: limited system feed-in. Applies to DC-coupled and AC-coupled feed-in.
com.victronenergy.settings | Feed excess DC-coupled PV into grid | 2707 | int16 | 1 |  | /Settings/Cgwacs/OvervoltageFeedIn | yes | 0=Don’t feed excess DC-tied PV into grid; 1=Feed excess DC-tied PV into the grid | Also known as Overvoltage Feed-in
com.victronenergy.settings | Don’t feed excess AC-coupled PV into grid | 2708 | int16 | 1 |  | /Settings/Cgwacs/PreventFeedback | yes | 0=Feed excess AC-tied PV into grid; 1=Don’t feed excess AC-tied PV into the grid | Formerly called Fronius Zero-Feedin
com.victronenergy.hub4 | Grid limiting status | 2709 | int16 | 1 |  | /PvPowerLimiterActive | no | 0=Feed-in limiting is inactive; 1=Feed-in limiting is active | Applies to both AC-coupled and DC-coupled limiting
com.victronenergy.settings | Limit managed battery voltage | 2710 | uint16 | 10 | 0 to 6553.5 | /Settings/SystemSetup/MaxChargeVoltage | yes | V DC | Only used if there is a managed battery in the system
com.victronenergy.settings | AC input 1 source (for VE.Bus inverter/chargers) | 2711 | uint16 | 1 | 0 to 65535 | /Settings/SystemSetup/AcInput1 | yes | 0=Unused;1=Grid;2=Genset;3=Shore | For Multi-RS, this is configured on the Inverter/Charger with VictronConnect
com.victronenergy.settings | AC input 2 source (for VE.Bus inverter/chargers) | 2712 | uint16 | 1 | 0 to 65535 | /Settings/SystemSetup/AcInput2 | yes | 0=Unused;1=Grid;2=Genset;3=Shore
com.victronenergy.gps | Latitude | 2800 | int32 | 10000000 | -214.7483648 to 214.7483648 | /Position/Latitude | no | Decimal degrees
com.victronenergy.gps | Longitude | 2802 | int32 | 10000000 | -214.7483648 to 214.7483648 | /Position/Longitude | no | Decimal degrees
com.victronenergy.gps | Course | 2804 | uint16 | 100 | 0 to 655.35 | /Course | no | Degrees | Direction of movement 0-360 degrees
com.victronenergy.gps | Speed | 2805 | uint16 | 100 | 0 to 655.35 | /Speed | no | m/s | Speed in m/s
com.victronenergy.gps | GPS fix | 2806 | uint16 | 1 | 0 to 65535 | /Fix | no |  | 0: no fix, 1: fix
com.victronenergy.gps | GPS number of satellites | 2807 | uint16 | 1 | 0 to 65535 | /NrOfSatellites | no
com.victronenergy.gps | Altitude | 2808 | int32 | 10 | -214748364.8 to 214748364.8 | /Altitude | no | m
com.victronenergy.settings | ESS BatteryLife state | 2900 | uint16 | 1 |  | /Settings/CGwacs/BatteryLife/State | yes | 0=Unused, BL disabled;1=Restarting;2=Self-consumption;3=Self-consumption;4=Self-consumption;5=Discharge disabled;6=Force charge;7=Sustain;8=Low Soc Recharge;9=Keep batteries charged;10=BL Disabled;11=BL Disabled (Low SoC);12=BL Disabled (Low SOC recharge) | Use value 0 (disable) and 1(enable) for writing only
com.victronenergy.settings | ESS Minimum SoC (unless grid fails) | 2901 | uint16 | 10 |  | /Settings/CGwacs/BatteryLife/MinimumSocLimit | yes | % | Same as the setting in the GUI
com.victronenergy.settings | ESS Mode | 2902 | uint16 | 1 | 0 to 65535 | /Settings/Cgwacs/Hub4Mode | yes | 1=ESS with Phase Compensation;2=ESS without phase compensation;3=Disabled/External Control
com.victronenergy.settings | ESS BatteryLife SoC limit (read only) | 2903 | uint16 | 10 |  | /Settings/Cgwacs/BatteryLife/SocLimit | no | % | This value is maintained by BatteryLife. The Active SOC limit is the lower of this value, and register 2901. Also see https://www.victronenergy.com/media/pg/Energy_Storage_System/en/controlling-depth-of-discharge.html#UUID-af4a7478-4b75-68ac-cf3c-16c381335d1e
com.victronenergy.tank | Product ID | 3000 | uint16 | 1 | 0 to 65535 | /ProductId | no
com.victronenergy.tank | Tank capacity | 3001 | uint32 | 10000 | 0 to 429496.7296 | /Capacity | no | m3
com.victronenergy.tank | Tank fluid type | 3003 | uint16 | 1 | 0 to 65535 | /FluidType | no | 0=Fuel;1=Fresh water;2=Waste water;3=Live well;4=Oil;5=Black water (sewage);6=Gasoline;7=Diesel;8=LPG;9=LNG;10=Hydraulic oil;11=Raw water
com.victronenergy.tank | Tank level | 3004 | uint16 | 10 | 0 to 6553.5 | /Level | no | %
com.victronenergy.tank | Tank remaining fluid | 3005 | uint32 | 10000 | 0 to 429496.7296 | /Remaining | no | m3
com.victronenergy.tank | Tank status | 3007 | uint16 | 1 | 0 to 65535 | /Status | no | 0=OK;1=Open circuit;2=Short circuited;3=Reverse Polarity;4=Unknown
com.victronenergy.inverter | Output current | 3100 | int16 | 10 | -3276.8 to 3276.8 | /Ac/Out/L1/I | no | A AC
com.victronenergy.inverter | Output voltage | 3101 | uint16 | 10 | 0 to 6553.6 | /Ac/Out/L1/V | no | V AC
com.victronenergy.inverter | Output power | 3102 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L1/P | no | W AC
com.victronenergy.inverter | Battery voltage | 3105 | uint16 | 100 | 0 to 655.36 | /Dc/0/Voltage | no | V DC
com.victronenergy.inverter | Battery current | 3106 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A DC
com.victronenergy.inverter | High temperature alarm | 3110 | uint16 | 1 | 0 to 65535 | /Alarms/HighTemperature | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter | High battery voltage alarm | 3111 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter | High AC-Out voltage alarm | 3112 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltageAcOut | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter | Low temperature alarm | 3113 | uint16 | 1 | 0 to 65535 | /Alarms/LowTemperature | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter | Low battery voltage alarm | 3114 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter | Low AC-Out voltage alarm | 3115 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltageAcOut | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter | Overload alarm | 3116 | uint16 | 1 | 0 to 65535 | /Alarms/Overload | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter | Ripple alarm | 3117 | uint16 | 1 | 0 to 65535 | /Alarms/Ripple | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter | Firmware version | 3125 | uint16 | 1 | 0 to 65535 | /FirmwareVersion | no
com.victronenergy.inverter | Inverter on/off/eco | 3126 | uint16 | 1 | 0 to 65535 | /Mode | yes | 2=On;4=Off;5=Eco
com.victronenergy.inverter | Inverter model | 3127 | uint16 | 1 | 0 to 65535 | /ProductId | no
com.victronenergy.inverter | Inverter state | 3128 | uint16 | 1 | 0 to 65535 | /State | no | 0=Off;1=Low power mode (search mode);2=Fault;9=Inverting (on)
com.victronenergy.inverter | Energy from battery to AC-out | 3130 | uint32 | 100 | 0 to 42949672.95 | /Energy/InverterToAcOut | no | kWh
com.victronenergy.inverter | Energy from AC-out to battery | 3132 | uint32 | 100 | 0 to 42949672.95 | /Energy/OutToInverter | no | kWh
com.victronenergy.inverter | Energy from solar to AC-out | 3134 | uint32 | 100 | 0 to 42949672.95 | /Energy/SolarToAcOut | no | kWh
com.victronenergy.inverter | Energy from solar to battery | 3136 | uint32 | 100 | 0 to 42949672.95 | /Energy/SolarToBattery | no | kWh
com.victronenergy.inverter | PV voltage (for single tracker units) | 3138 | uint16 | 10 | 0 to 6553.5 | /Pv/V | no | V DC
com.victronenergy.inverter | PV voltage for tracker 0 | 3140 | uint16 | 10 | 0 to 6553.5 | /Pv/0/V | no | V DC
com.victronenergy.inverter | PV voltage for tracker 1 | 3141 | uint16 | 10 | 0 to 6553.5 | /Pv/1/V | no | V DC
com.victronenergy.inverter | PV voltage for tracker 2 | 3142 | uint16 | 10 | 0 to 6553.5 | /Pv/2/V | no | V DC
com.victronenergy.inverter | PV voltage for tracker 3 | 3143 | uint16 | 10 | 0 to 6553.5 | /Pv/3/V | no | V DC
com.victronenergy.inverter | Yield today for today on tracker 0 | 3148 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/0/Yield | no | kWh
com.victronenergy.inverter | Yield today for today on tracker 1 | 3149 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/1/Yield | no | kWh
com.victronenergy.inverter | Yield today for today on tracker 2 | 3150 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/2/Yield | no | kWh
com.victronenergy.inverter | Yield today for today on tracker 3 | 3151 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/3/Yield | no | kWh
com.victronenergy.inverter | Yield today for yesterday on tracker 0 | 3152 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/0/Yield | no | kWh
com.victronenergy.inverter | Yield today for yesterday on tracker 1 | 3153 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/1/Yield | no | kWh
com.victronenergy.inverter | Yield today for yesterday on tracker 2 | 3154 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/2/Yield | no | kWh
com.victronenergy.inverter | Yield today for yesterday on tracker 3 | 3155 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/3/Yield | no | kWh
com.victronenergy.inverter | Maximum power for today on tracker 0 | 3156 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/0/MaxPower | no | W
com.victronenergy.inverter | Maximum power for today on tracker 1 | 3157 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/1/MaxPower | no | W
com.victronenergy.inverter | Maximum power for today on tracker 2 | 3158 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/2/MaxPower | no | W
com.victronenergy.inverter | Maximum power for today on tracker 3 | 3159 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/3/MaxPower | no | W
com.victronenergy.inverter | Maximum power for yesterday on tracker 0 | 3160 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/0/MaxPower | no | W
com.victronenergy.inverter | Maximum power for yesterday on tracker 1 | 3161 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/1/MaxPower | no | W
com.victronenergy.inverter | Maximum power for yesterday on tracker 2 | 3162 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/2/MaxPower | no | W
com.victronenergy.inverter | Maximum power for yesterday on tracker 3 | 3163 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/3/MaxPower | no | W
com.victronenergy.inverter | PV power for tracker 0 | 3164 | uint16 | 1 | 0 to 65535 | /Pv/0/P | no | W
com.victronenergy.inverter | PV power for tracker 1 | 3165 | uint16 | 1 | 0 to 65535 | /Pv/1/P | no | W
com.victronenergy.inverter | PV power for tracker 2 | 3166 | uint16 | 1 | 0 to 65535 | /Pv/2/P | no | W
com.victronenergy.inverter | PV power for tracker 3 | 3167 | uint16 | 1 | 0 to 65535 | /Pv/3/P | no | W
com.victronenergy.inverter | Low SOC alarm | 3168 | uint16 | 1 | 0 to 65535 | /Alarms/LowSoc | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter | MPP operation mode tracker 1 | 3169 | uint16 | 1 | 0 to 65535 | /Pv/0/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.inverter | MPP operation mode tracker 2 | 3170 | uint16 | 1 | 0 to 65535 | /Pv/1/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.inverter | MPP operation mode tracker 3 | 3171 | uint16 | 1 | 0 to 65535 | /Pv/2/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.inverter | MPP operation mode tracker 4 | 3172 | uint16 | 1 | 0 to 65535 | /Pv/3/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.genset | Phase 1 voltage | 3200 | uint16 | 10 | 0 to 6553.6 | /Ac/L1/Voltage | no | V AC
com.victronenergy.genset | Phase 2 voltage | 3201 | uint16 | 10 | 0 to 6553.6 | /Ac/L2/Voltage | no | V AC
com.victronenergy.genset | Phase 3 voltage | 3202 | uint16 | 10 | 0 to 6553.6 | /Ac/L3/Voltage | no | V AC
com.victronenergy.genset | Phase 1 current | 3203 | int16 | 10 | -3276.8 to 3276.8 | /Ac/L1/Current | no | A AC
com.victronenergy.genset | Phase 2 current | 3204 | int16 | 10 | -3276.8 to 3276.8 | /Ac/L2/Current | no | A AC
com.victronenergy.genset | Phase 3 current | 3205 | int16 | 10 | -3276.8 to 3276.8 | /Ac/L3/Current | no | A AC
com.victronenergy.genset | Phase 1 power | 3206 | int16 | 1 | -32768 to 32768 | /Ac/L1/Power | no | W
com.victronenergy.genset | Phase 2 power | 3207 | int16 | 1 | -32768 to 32768 | /Ac/L2/Power | no | W
com.victronenergy.genset | Phase 3 power | 3208 | int16 | 1 | -32768 to 32768 | /Ac/L3/Power | no | W
com.victronenergy.genset | AC Frequency | 3209 | uint16 | 100 | 0 to 655.36 | /Ac/Frequency | no | Hz
com.victronenergy.genset | RESERVED | 3210 | uint16 |  |  |  | no
com.victronenergy.genset | RESERVED | 3211 | uint16 |  |  |  | no
com.victronenergy.genset | Generator model | 3212 | uint16 | 1 | 0 to 65535 | /ProductId | no
com.victronenergy.genset | Status | 3213 | uint16 | 1 | 0 to 65535 | /StatusCode | no | 0=Standby;1=Startup 1;2=Startup 2;3=Startup 3;4=Startup 4;5=Startup 5;6=Startup 6;7=Startup 7;8=Running;9=Stopping;10=Error
com.victronenergy.genset | Error | 3214 | uint16 | 1 | 0 to 65535 | /ErrorCode | no | 0=No error;1=AC voltage L1 too low;2=AC frequency L1 too low;3=AC current too low;4=AC power too low;5=Emergency stop;6=Servo current too low;7=Oil pressure too low;8=Engine temperature too low;9=Winding temperature too low;10=Exhaust temperature too low;13=Starter current too low;14=Glow current too low;15=Glow current too low;16=Fuel holding magnet current too low;17=Stop solenoid hold coil current too low;18=Stop solenoid pull coil current too low;19=Optional DC out current too low;20=5V output voltage too low;21=Boost output current too low;22=Panel supply current too high;25=Starter battery voltage too low;26=Startup aborted (rotation too low);28=Rotation too low;29=Power contactor current too low;30=AC voltage L2 too low;31=AC frequency L2 too low;32=AC current L2 too low;33=AC power L2 too low;34=AC voltage L3 too low;35=AC frequency L3 too low;36=AC current L3 too low;37=AC power L3 too low;62=Fuel temperature too low;63=Fuel level too low;65=AC voltage L1 too high;66=AC frequency too high;67=AC current too high;68=AC power too high;70=Servo current too high;71=Oil pressure too high;72=Engine temperature too high;73=Winding temperature too high;74=Exhaust temperature too low;77=Starter current too low;78=Glow current too high;79=Glow current too high;80=Fuel holding magnet current too high;81=Stop solenoid hold coil current too high;82=Stop solenoid pull coil current too high;83=Optional DC out current too high;84=5V output voltage too high;85=Boost output current too high;89=Starter battery voltage too high;90=Startup aborted (rotation too high);92=Rotation too high;93=Power contactor current too high;94=AC voltage L2 too high;95=AC frequency L2 too high;96=AC current L2 too high;97=AC power L2 too high;98=AC voltage L3 too high;99=AC frequency L3 too high;100=AC current L3 too high;101=AC power L3 too high;126=Fuel temperature too high;127=Fuel level too high;130=Lost control unit;131=Lost panel;132=Service needed;133=Lost 3-phase module;134=Lost AGT module;135=Synchronization failure;137=Intake airfilter;139=Lost sync. module;140=Load-balance failed;141=Sync-mode deactivated;142=Engine controller;148=Rotating field wrong;149=Fuel level sensor lost;150=Init failed;151=Watchdog;152=Out: winding;153=Out: exhaust;154=Out: Cyl. head;155=Inverter over temperature;156=Inverter overload;157=Inverter communication lost;158=Inverter sync failed;159=CAN communication lost;160=L1 overload;161=L2 overload;162=L3 overload;163=DC overload;164=DC overvoltage;165=Emergency stop;166=No connection
com.victronenergy.genset | Auto start | 3215 | uint16 | 1 | 0 to 65535 | /RemoteStartModeEnabled | no | 0=Disabled;1=Enabled
com.victronenergy.genset | Engine load | 3216 | uint16 | 1 | 0 to 65535 | /Engine/Load | no | %
com.victronenergy.genset | Engine speed | 3217 | uint16 | 1 | 0 to 65535 | /Engine/Speed | no | RPM
com.victronenergy.genset | Engine operating hours | 3218 | uint16 | 0.01 | 0 to 6553500 | /Engine/OperatingHours | no | s
com.victronenergy.genset | Engine coolant temperature | 3219 | int16 | 10 | -3276.8 to 3276.8 | /Engine/CoolantTemperature | no | Degrees celsius
com.victronenergy.genset | Engine winding temperature | 3220 | int16 | 10 | -3276.8 to 3276.8 | /Engine/WindingTemperature | no | Degrees celsius
com.victronenergy.genset | Engine exhaust temperature | 3221 | int16 | 10 | -3276.8 to 3276.8 | /Engine/ExaustTemperature | no | Degrees celsius
com.victronenergy.genset | Starter voltage | 3222 | uint16 | 100 | 0 to 655.36 | /StarterVoltage | no | V DC
com.victronenergy.genset | Start generator | 3223 | uint16 | 1 | 0 to 65535 | /Start | yes | 0=Stop;1=Start | This is normally controlled by the start/stop service. In Venus 3.00 and later, use com.victronenergy.generator/ManualStart instead.
com.victronenergy.genset | Oil pressure | 3224 | int16 | 1 | -32768 to 32768 | /Engine/OilPressure | no | kPa
com.victronenergy.genset | RESERVED | 3225 | uint16 | 1 |  | RESERVED | no
com.victronenergy.genset | RESERVED | 3226 | uint16 | 1 |  | RESERVED | no
com.victronenergy.genset | RESERVED | 3227 | uint16 | 1 |  | RESERVED | no | Degrees celsius
com.victronenergy.genset | Engine oil temperature | 3228 | int16 | 1 | -32768 to 32767 | /Engine/OilTemperature | no | Degrees celsius
com.victronenergy.genset | 1st Error string (for third party gensets) | 5000 | string[16] |  | 32 characters | /Error/0/Id | no | See https://github.com/victronenergy/venus/wiki/dbus#error-codes
com.victronenergy.genset | 2nd Error string (for third party gensets) | 5016 | string[16] |  | 32 characters | /Error/1/Id | no
com.victronenergy.genset | 3rd Error string (for third party gensets) | 5032 | string[16] |  | 32 characters | /Error/2/Id | no
com.victronenergy.genset | 4th Error string (for third party gensets) | 5048 | string[16] |  | 32 characters | /Error/3/Id | no
com.victronenergy.genset | 5th Error string (for third party gensets) | 5064 | string[16] |  | 32 characters | /Error/4/Id | no
com.victronenergy.genset | 6th Error string (for third party gensets) | 5080 | string[16] |  | 32 characters | /Error/5/Id | no
com.victronenergy.genset | 7th Error string (for third party gensets) | 5096 | string[16] |  | 32 characters | /Error/6/Id | no
com.victronenergy.genset | 8th Error string (for third party gensets) | 5112 | string[16] |  | 32 characters | /Error/7/Id | no
com.victronenergy.temperature | Product ID | 3300 | uint16 | 1 | 0 to 65535 | /ProductId | no
com.victronenergy.temperature | Temperature scale factor | 3301 | uint16 | 100 | 0 to 655.35 | /Scale | no
com.victronenergy.temperature | Temperature offset | 3302 | int16 | 100 | -327.68 to 327.67 | /Offset | no
com.victronenergy.temperature | Temperature type | 3303 | uint16 | 1 | 0 to 65535 | /TemperatureType | no | 0=Battery;1=Fridge;2=Generic
com.victronenergy.temperature | Temperature | 3304 | int16 | 100 | -327.68 to 327.67 | /Temperature | no | Degrees celsius
com.victronenergy.temperature | Temperature status | 3305 | uint16 | 1 | 0 to 65535 | /Status | no | 0=OK;1=Open circuit;2=Short circuited;3=Reverse Polarity;4=Unknown
com.victronenergy.temperature | Humidity | 3306 | uint16 | 10 | 0 to 6553.3 | /Humidity | no | % | Relative humidity as a percentage. Only available on sensors that has this feature, eg Ruuvi.
com.victronenergy.temperature | Sensor battery voltage | 3307 | uint16 | 100 | 0 to 655.35 | /BatteryVoltage | no | V | Used by wireless tags that have a battery in the sensor
com.victronenergy.temperature | Atmospheric pressure | 3308 | uint16 | 1 | 0 to 65535 | /Pressure | no | hPa | Only available on sensors that has this feature, eg Ruuvi.
com.victronenergy.pulsemeter | Aggregate (measured value) | 3400 | uint32 | 1 | 0 to 4294967295 | /Aggregate | no | m3
com.victronenergy.pulsemeter | Count (number of pulses on meter) | 3402 | uint32 | 1 | 0 to 4294967295 | /Count | no
com.victronenergy.digitalinput | Count | 3420 | uint32 | 1 | 0 to 4294967295 | /Count | no
com.victronenergy.digitalinput | State | 3422 | uint16 | 1 | 0 to 1 | /State | no | 0=Low;1=High;2=Off;3=On;4=No;5=Yes;6=Open;7=Closed;8=Alarm;9=OK;10=Running;11=Stopped
com.victronenergy.digitalinput | Alarm | 3423 | uint16 | 1 | 0 to 2 | /Alarm | no | 0=No alarm;2=Alarm
com.victronenergy.digitalinput | Type | 3424 | uint16 | 1 | 0 to 65535 | /Type | no | 2=Door;3=Bilge pump;4=Bilge alarm;5=Burglar alarm;6=Smoke alarm;7=Fire alarm;8=CO2 alarm;9=Generator
com.victronenergy.generator | Manual Start | 3500 | uint16 | 1 | 0 to 1 | /ManualStart | yes | 0=Stop generator; 1=Start generator
com.victronenergy.generator | Condition that started the generator | 3501 | uint16 | 1 | 0 to 65535 | /RunningByConditionCode | no | 0=Stopped;1=Manual;2=TestRun;3=LossOfComms;4=Soc;5=AcLoad;6=BatteryCurrent;7=BatteryVoltage;8=InverterTemperatur;9=InverterOverload;10=StopOnAc1
com.victronenergy.generator | Runtime in seconds | 3502 | uint16 | 1 | 0 to 65535 | /Runtime | no | seconds
com.victronenergy.generator | Quiet hours active | 3503 | uint16 | 1 | 0 to 65535 | /QuietHours | no | 0=Quiet hours inactive; 1=Quiet hours active
com.victronenergy.generator | Runtime in seconds | 3504 | uint32 | 1 | 0 to 4294967295 | /Runtime | no | seconds
com.victronenergy.generator | Generator start/stop state | 3506 | uint16 | 1 | 0 to 65535 | /State | no | 0=Stopped;1=Running;2=Warmup;3=Cooldown;4=Stopping;10=Error
com.victronenergy.generator | Generator remote error | 3507 | uint16 | 1 | 0 to 65535 | /Error | no | 0=No Error;1=Remote disabled;2=Remote fault | Only used for FisherPanda gensets
com.victronenergy.generator | Generator not detected at AC input alarm | 3508 | uint16 | 1 | 0 to 65535 | /Alarms/NoGeneratorAtAcIn | no | 0=No alarm;2=Alarm
com.victronenergy.generator | Auto start enabled/disabled | 3509 | uint16 | 1 | 0 to 65535 | /AutoStartEnabled | yes | 0=Autostart disabled; 1=Autostart enabled
com.victronenergy.generator | Service countdown counter | 3510 | uint32 | 1 | 0 to 65535 | /ServiceCounter | no | seconds until next generator service
com.victronenergy.generator | Service countdown reset | 3512 | uint16 | 1 | 0 to 65535 | /ServiceCounterReset | yes | 1=Reset service counter
com.victronenergy.meteo | Solar irradiance | 3600 | uint16 | 10 | 0 to 6553.5 | /Irradiance | no | W/m^2
com.victronenergy.meteo | Wind speed | 3601 | uint16 | 10 | 0 to 6553.5 | /WindSpeed | no | m/s
com.victronenergy.meteo | Cell temperature of sensor | 3602 | int16 | 10 | -3276.8 to 3276.7 | /CellTemperature | no | Degrees celsius
com.victronenergy.meteo | External temperature | 3603 | int16 | 10 | -3276.8 to 3276.7 | /ExternalTemperature | no | Degrees celsius
com.victronenergy.meteo | External temperature – second sensor | 3604 | int16 | 10 | -3276.8 to 3276.7 | /ExternalTemperature2 | no | Degrees celsius | Only available on IMT SI-RS485TC-3T-MB running firmware 2.01 or later
com.victronenergy.evcharger | Product ID | 3800 | uint16 | 1 | 0 to 65535 | /ProductId | no
com.victronenergy.evcharger | Firmware version | 3802 | uint32 | 1 | 0 to 4294967295 | /FirmwareVersion | no
com.victronenergy.evcharger | Serial | 3804 | string[6] | 1 |  | /Serial | no
com.victronenergy.evcharger | Model | 3810 | string[4] | 1 |  | /Model | no
com.victronenergy.evcharger | Maximum charge current | 3814 | uint16 | 1 | 0 to 65535 | /MaxCurrent | yes | A
com.victronenergy.evcharger | Mode | 3815 | uint16 | 1 | 0 to 65535 | /Mode | yes | 0=Manual;1=Auto
com.victronenergy.evcharger | Energy consumed by charger | 3816 | uint32 | 100 | 0 to 42949672.95 | /Ac/Energy/Forward | no | kWh
com.victronenergy.evcharger | L1 Power | 3818 | uint16 | 1 | 0 to 65535 | /Ac/L1/Power | no | W
com.victronenergy.evcharger | L2 Power | 3819 | uint16 | 1 | 0 to 65535 | /Ac/L2/Power | no | W
com.victronenergy.evcharger | L3 Power | 3820 | uint16 | 1 | 0 to 65535 | /Ac/L3/Power | no | W
com.victronenergy.evcharger | Total power | 3821 | uint16 | 1 | 0 to 65535 | /Ac/Power | no | W
com.victronenergy.evcharger | Charging time | 3822 | uint16 | 0.01 | 0 to 6553500 | /ChargingTime | no | seconds
com.victronenergy.evcharger | Charge current | 3823 | uint16 | 1 | 0 to 65535 | /Current | no | A
com.victronenergy.evcharger | Status | 3824 | uint16 | 1 | 0 to 65535 | /Status | no | 0=Disconnected; 1=Connected; 2=Charging; 3=Charged; 4=Waiting for sun; 5=Waiting for RFID; 6=Waiting for start; 7=Low SOC; 8=Ground test error; 9=Welded contacts test error; 10=CP input test error (shorted); 11=Residual current detected; 12=Undervoltage detected; 13=Overvoltage detected; 14=Overheating detected; 15=Reserved; 16=Reserved; 17=Reserved; 18=Reserved; 19=Reserved; 20=Charging limit; 21=Start charging; 22=Switching to 3 phase; 23=Switching to 1 phase; 24=Stop charging
com.victronenergy.evcharger | Set charge current (manual mode) | 3825 | uint16 | 1 | 0 to 65535 | /SetCurrent | yes | A
com.victronenergy.evcharger | Start/stop charging (manual mode) | 3826 | uint16 | 1 | 0 to 65535 | /StartStop | yes | 0=Stop;1=Start
com.victronenergy.evcharger | Position | 3827 | uint16 | 1 | 0 to 65535 | /Position | yes | 0=AC input 1;1=AC output;2=AC input 2
com.victronenergy.acload | L1 Power | 3900 | uint16 | 1 | 0 to 65535 | /Ac/L1/Power | no | W
com.victronenergy.acload | L2 Power | 3901 | uint16 | 1 | 0 to 65535 | /Ac/L2/Power | no | W
com.victronenergy.acload | L3 Power | 3902 | uint16 | 1 | 0 to 65535 | /Ac/L3/Power | no | W
com.victronenergy.acload | Serial number | 3903 | string[7] |  |  | /Serial | no
com.victronenergy.acload | L1 Voltage | 3910 | uint16 | 10 | 0 to 6553.5 | /Ac/L1/Voltage | no | V AC
com.victronenergy.acload | L1 Current | 3911 | in16 | 10 | -3276.8 to 3276.7 | /Ac/L1/Current | no | A
com.victronenergy.acload | L2 Voltage | 3912 | uint16 | 10 | 0 to 6553.5 | /Ac/L2/Voltage | no | V AC
com.victronenergy.acload | L2 Current | 3913 | in16 | 10 | -3276.8 to 3276.7 | /Ac/L2/Current | no | A
com.victronenergy.acload | L3 Voltage | 3914 | uint16 | 10 | 0 to 6553.5 | /Ac/L3/Voltage | no | V AC
com.victronenergy.acload | L3 Current | 3915 | in16 | 10 | -3276.8 to 3276.7 | /Ac/L3/Current | no | A
com.victronenergy.acload | L1 Energy | 3916 | uint32 | 100 | 0 to 42949672.95 | /Ac/L1/Energy/Forward | no | kWh
com.victronenergy.acload | L2 Energy | 3918 | uint32 | 100 | 0 to 42949672.95 | /Ac/L2/Energy/Forward | no | kWh
com.victronenergy.acload | L3 Energy | 3920 | uint32 | 100 | 0 to 42949672.95 | /Ac/L3/Energy/Forward | no | kWh
com.victronenergy.fuelcell | Battery voltage | 4000 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.fuelcell | Battery current | 4001 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A
com.victronenergy.fuelcell | Auxiliary voltage | 4002 | uint16 | 100 | 0 to 655.35 | /Dc/1/Voltage | no | V DC
com.victronenergy.fuelcell | Temperature | 4003 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius
com.victronenergy.fuelcell | Total energy produced | 4004 | uint32 | 100 | 0 to 42949672.95 | /History/EnergyOut | no | kWh
com.victronenergy.fuelcell | Low voltage alarm | 4006 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.fuelcell | High voltage alarm | 4007 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.fuelcell | Low auxiliary voltage alarm | 4008 | uint16 | 1 | 0 to 65535 | /Alarms/LowStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.fuelcell | High auxiliary voltage alarm | 4009 | uint16 | 1 | 0 to 65535 | /Alarms/HighStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.fuelcell | Low temperature alarm | 4010 | uint16 | 1 | 0 to 65535 | /Alarms/LowTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.fuelcell | High temperature alarm | 4011 | uint16 | 1 | 0 to 65535 | /Alarms/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.alternator | Battery voltage | 4100 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.alternator | Battery current | 4101 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A
com.victronenergy.alternator | Auxiliary voltage | 4102 | uint16 | 100 | 0 to 655.35 | /Dc/1/Voltage | no | V DC
com.victronenergy.alternator | Temperature | 4103 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius
com.victronenergy.alternator | Total energy produced | 4104 | uint32 | 100 | 0 to 42949672.95 | /History/EnergyOut | no | kWh
com.victronenergy.alternator | Low voltage alarm | 4106 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.alternator | High voltage alarm | 4107 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.alternator | Low auxiliary voltage alarm | 4108 | uint16 | 1 | 0 to 65535 | /Alarms/LowStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.alternator | High auxiliary voltage alarm | 4109 | uint16 | 1 | 0 to 65535 | /Alarms/HighStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.alternator | Low temperature alarm | 4110 | uint16 | 1 | 0 to 65535 | /Alarms/LowTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.alternator | High temperature alarm | 4111 | uint16 | 1 | 0 to 65535 | /Alarms/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.alternator | Alternator state | 4112 | uint16 | 1 | 0 to 65535 | /State | no | 0=Off;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;11=Power Supply;252=External control
com.victronenergy.alternator | Alternator error code | 4113 | uint16 | 1 | 0 to 65535 | /ErrorCode | no | 12=High battery temperature;13=High battery voltage;14=Low battery voltage;15=VBat exceeds $CPB;21=High alternator temperature;22=Alternator overspeed;24=Internal error;41=High field FET temperature;42=Sensor missing;43=Low VAlt;44=High Voltage offset;45=VAlt exceeds $CPB;51-52=Battery disconnect request;53=Battery instance out of range;54=Too many BMSes;55=AEBus fault;56=Too many Victron devices;58-61=Battery requested disconnection;91=BMS lost;92=Forced idle;201=DCDC converter fail;201-207=DCDC error
com.victronenergy.alternator | Engine speed | 4114 | uint16 | 1 | 0 to 65535 | /Engine/Speed | no | RPM
com.victronenergy.alternator | Alternator speed | 4115 | uint16 | 1 | 0 to 65535 | /Speed | no | RPM
com.victronenergy.alternator | Percentage field drive | 4116 | uint16 | 1 | 0 to 65535 | /FieldDrive | no | %
com.victronenergy.alternator | Input voltage (before DC/DC converter) | 4117 | uint16 | 100 | 0 to 655.35 | /Dc/In/V | no | V DC
com.victronenergy.alternator | Input power | 4118 | uint16 | 1 | 0 to 65535 | /Dc/In/P | no | W DC
com.victronenergy.alternator | Mode | 4119 | uint16 | 1 | 0 to 65535 | /Mode | no | 1=On;4=Off
com.victronenergy.alternator | Cumulative amp-hours charged | 4120 | uint32 | 10 | 0 to 429496729.5 | /History/Cumulative/User/ChargedAh | no | Ah
com.victronenergy.dcsource | Battery voltage | 4200 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.dcsource | Battery current | 4201 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A
com.victronenergy.dcsource | Auxiliary voltage | 4202 | uint16 | 100 | 0 to 655.35 | /Dc/1/Voltage | no | V DC
com.victronenergy.dcsource | Temperature | 4203 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius
com.victronenergy.dcsource | Total energy produced | 4204 | uint32 | 100 | 0 to 42949672.95 | /History/EnergyOut | no | kWh
com.victronenergy.dcsource | Low voltage alarm | 4206 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcsource | High voltage alarm | 4207 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcsource | Low auxiliary voltage alarm | 4208 | uint16 | 1 | 0 to 65535 | /Alarms/LowStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcsource | High auxiliary voltage alarm | 4209 | uint16 | 1 | 0 to 65535 | /Alarms/HighStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcsource | Low temperature alarm | 4210 | uint16 | 1 | 0 to 65535 | /Alarms/LowTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcsource | High temperature alarm | 4211 | uint16 | 1 | 0 to 65535 | /Alarms/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcload | Battery voltage | 4300 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.dcload | Battery current | 4301 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A
com.victronenergy.dcload | Auxiliary voltage | 4302 | uint16 | 100 | 0 to 655.35 | /Dc/1/Voltage | no | V DC
com.victronenergy.dcload | Temperature | 4303 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius
com.victronenergy.dcload | Total energy consumed | 4304 | uint32 | 100 | 0 to 42949672.95 | /History/EnergyIn | no | kWh
com.victronenergy.dcload | Low voltage alarm | 4306 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcload | High voltage alarm | 4307 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcload | Low auxiliary voltage alarm | 4308 | uint16 | 1 | 0 to 65535 | /Alarms/LowStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcload | High auxiliary voltage alarm | 4309 | uint16 | 1 | 0 to 65535 | /Alarms/HighStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcload | Low temperature alarm | 4310 | uint16 | 1 | 0 to 65535 | /Alarms/LowTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcload | High temperature alarm | 4311 | uint16 | 1 | 0 to 65535 | /Alarms/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcsystem | Battery voltage | 4400 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.dcsystem | Battery current | 4401 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A
com.victronenergy.dcsystem | Auxiliary voltage | 4402 | uint16 | 100 | 0 to 655.35 | /Dc/1/Voltage | no | V DC
com.victronenergy.dcsystem | Temperature | 4403 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius
com.victronenergy.dcsystem | Total energy produced | 4404 | uint32 | 100 | 0 to 42949672.95 | /History/EnergyOut | no | kWh
com.victronenergy.dcsystem | Total energy consumed | 4406 | uint32 | 100 | 0 to 42949672.95 | /History/EnergyIn | no | kWh
com.victronenergy.dcsystem | Low voltage alarm | 4408 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=No alarm;1=Warning; 2=Alarm
com.victronenergy.dcsystem | High voltage alarm | 4409 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=No alarm;1=Warning; 2=Alarm
com.victronenergy.dcsystem | Low auxiliary voltage alarm | 4410 | uint16 | 1 | 0 to 65535 | /Alarms/LowStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcsystem | High auxiliary voltage alarm | 4411 | uint16 | 1 | 0 to 65535 | /Alarms/HighStarterVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcsystem | Low temperature alarm | 4412 | uint16 | 1 | 0 to 65535 | /Alarms/LowTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcsystem | High temperature alarm | 4413 | uint16 | 1 | 0 to 65535 | /Alarms/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.multi | Input voltage phase 1 | 4500 | uint16 | 10 | 0 to 6553.5 | /Ac/In/1/L1/V | no | V AC
com.victronenergy.multi | Input voltage phase 2 | 4501 | uint16 | 10 | 0 to 6553.5 | /Ac/In/1/L2/V | no | V AC
com.victronenergy.multi | Input voltage phase 3 | 4502 | uint16 | 10 | 0 to 6553.5 | /Ac/In/1/L3/V | no | V AC
com.victronenergy.multi | Input current phase 1 | 4503 | int16 | 10 | 0 to 6553.5 | /Ac/In/1/L1/I | no | A AC
com.victronenergy.multi | Input current phase 2 | 4504 | int16 | 10 | 0 to 6553.5 | /Ac/In/1/L2/I | no | A AC
com.victronenergy.multi | Input current phase 3 | 4505 | int16 | 10 | 0 to 6553.5 | /Ac/In/1/L3/I | no | A AC
com.victronenergy.multi | Input power phase 1 | 4506 | int16 | 0.1 | -327680 to 327670 | /Ac/In/1/L1/P | no | W
com.victronenergy.multi | Input power phase 2 | 4507 | int16 | 0.1 | -327680 to 327670 | /Ac/In/1/L2/P | no | W
com.victronenergy.multi | Input power phase 3 | 4508 | int16 | 0.1 | -327680 to 327670 | /Ac/In/1/L3/P | no | W
com.victronenergy.multi | Input frequency | 4509 | uint16 | 100 |  | /Ac/In/1/L1/F | no | Hz
com.victronenergy.multi | Output voltage phase 1 | 4510 | uint16 | 10 | 0 to 6553.5 | /Ac/Out/L1/V | no | V AC
com.victronenergy.multi | Output voltage phase 2 | 4511 | uint16 | 10 | 0 to 6553.5 | /Ac/Out/L2/V | no | V AC
com.victronenergy.multi | Output voltage phase 3 | 4512 | uint16 | 10 | 0 to 6553.5 | /Ac/Out/L3/V | no | V AC
com.victronenergy.multi | Output current phase 1 | 4513 | int16 | 10 | 0 to 6553.5 | /Ac/Out/L1/I | no | A AC
com.victronenergy.multi | Output current phase 2 | 4514 | int16 | 10 | 0 to 6553.5 | /Ac/Out/L2/I | no | A AC
com.victronenergy.multi | Output current phase 3 | 4515 | int16 | 10 | 0 to 6553.5 | /Ac/Out/L3/I | no | A AC
com.victronenergy.multi | Output power phase 1 | 4516 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L1/P | no | W
com.victronenergy.multi | Output power phase 2 | 4517 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L2/P | no | W
com.victronenergy.multi | Output power phase 3 | 4518 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L3/P | no | W
com.victronenergy.multi | Output frequency | 4519 | uint16 | 100 | 0 to 655.35 | /Ac/Out/L1/F | no | Hz
com.victronenergy.multi | AC input 1 source type | 4520 | uint16 | 1 | 0 to 65535 | /Ac/In/1/Type | no | 0=Unused;1=Grid;2=Genset;3=Shore
com.victronenergy.multi | AC input 2 source type | 4521 | uint16 | 1 | 0 to 65535 | /Ac/In/2/Type | no | 0=Unused;1=Grid;2=Genset;3=Shore
com.victronenergy.multi | Ac input 1 current limit | 4522 | uint16 | 10 | 0 to 6553.5 | /Ac/In/1/CurrentLimit | yes | A
com.victronenergy.multi | Ac input 2 current limit | 4523 | uint16 | 10 | 0 to 6553.5 | /Ac/In/2/CurrentLimit | yes | A
com.victronenergy.multi | Phase count | 4524 | uint16 | 1 | 0 to 65535 | /Ac/NumberOfPhases | no | count
com.victronenergy.multi | Active AC input | 4525 | uint16 | 1 | 0 to 65535 | /Ac/ActiveIn/ActiveInput | no | 0=AC Input 1;1=AC Input 2;240=Disconnected
com.victronenergy.multi | Battery voltage | 4526 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.multi | Battery current | 4527 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A DC
com.victronenergy.multi | Battery temperature | 4528 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius
com.victronenergy.multi | Battery State of Charge | 4529 | uint16 | 10 | 0 to 6553.5 | /Soc | no | %
com.victronenergy.multi | Inverter/Charger state | 4530 | uint16 | 1 | 0 to 65535 | /State | no | 0=Off;1=Low Power;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;8=Passthru;9=Inverting;10=Power assist;11=Power supply;252=External control
com.victronenergy.multi | Switch position | 4531 | uint16 | 1 | 0 to 65535 | /Mode | yes | 1=Charger Only;2=Inverter Only;3=On;4=Off
com.victronenergy.multi | Temperature alarm | 4532 | uint16 | 1 | 0 to 65535 | /Alarms/HighTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.multi | High voltage alarm | 4533 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.multi | High AC-Out voltage alarm | 4534 | uint16 | 1 | 0 to 65535 | /Alarms/HighVoltageAcOut | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.multi | Low battery temperature alarm | 4535 | uint16 | 1 | 0 to 65535 | /Alarms/LowTemperature | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.multi | Low voltage alarm | 4536 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltage | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.multi | Low AC-Out voltage alarm | 4537 | uint16 | 1 | 0 to 65535 | /Alarms/LowVoltageAcOut | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.multi | Overload alarm | 4538 | uint16 | 1 | 0 to 65535 | /Alarms/Overload | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.multi | High DC ripple alarm | 4539 | uint16 | 1 | 0 to 65535 | /Alarms/Ripple | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.multi | PV power | 4540 | uint16 | 1 | 0 to 65535 | /Yield/Power | no | W
com.victronenergy.multi | User yield | 4541 | uint16 | 10 | 0 to 6553.5 | /Yield/User | no | kWh
com.victronenergy.multi | Relay on the Multi RS | 4542 | uint16 | 1 | 0 to 65535 | /Relay/0/State | no | 0=Open;1=Closed
com.victronenergy.multi | MPP operation mode | 4543 | uint16 | 1 | 0 to 65535 | /MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.multi | PV voltage | 4544 | uint16 | 10 | 0 to 6553.5 | /Pv/V | no | V DC
com.victronenergy.multi | Error code | 4545 | uint16 | 1 | 0 to 65535 | /ErrorCode | no | 0=No error;1=Battery temperature too high;2=Battery voltage too high;3=Battery temperature sensor miswired (+);4=Battery temperature sensor miswired (-);5=Battery temperature sensor disconnected;6=Battery voltage sense miswired (+);7=Battery voltage sense miswired (-);8=Battery voltage sense disconnected;9=Battery voltage wire losses too high;17=Charger temperature too high;18=Charger over-current;19=Charger current polarity reversed;20=Bulk time limit reached;22=Charger temperature sensor miswired;23=Charger temperature sensor disconnected;34=Input current too high
com.victronenergy.multi | Energy from AC-in-1 to AC-out | 4546 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcIn1ToAcOut | no | kWh
com.victronenergy.multi | Energy from AC-in-1 to battery | 4548 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcIn1ToInverter | no | kWh
com.victronenergy.multi | Energy from AC-in-2 to AC-out | 4550 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcIn2ToAcOut | no | kWh
com.victronenergy.multi | Energy from AC-in-2 to battery | 4552 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcIn2ToInverter | no | kWh
com.victronenergy.multi | Energy from AC-out to AC-in-1 | 4554 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcOutToAcIn1 | no | kWh
com.victronenergy.multi | Energy from AC-out to AC-in-2 | 4556 | uint32 | 100 | 0 to 42949672.96 | /Energy/AcOutToAcIn2 | no | kWh
com.victronenergy.multi | Energy from battery to AC-in-1 | 4558 | uint32 | 100 | 0 to 42949672.96 | /Energy/InverterToAcIn1 | no | kWh
com.victronenergy.multi | Energy from battery to AC-in-2 | 4560 | uint32 | 100 | 0 to 42949672.96 | /Energy/InverterToAcIn2 | no | kWh
com.victronenergy.multi | Energy from battery to AC-out | 4562 | uint32 | 100 | 0 to 42949672.96 | /Energy/InverterToAcOut | no | kWh
com.victronenergy.multi | Energy from AC-out to battery | 4564 | uint32 | 100 | 0 to 42949672.96 | /Energy/OutToInverter | no | kWh
com.victronenergy.multi | Energy from solar to AC-in-1 | 4566 | uint32 | 100 | 0 to 42949672.96 | /Energy/SolarToAcIn1 | no | kWh
com.victronenergy.multi | Energy from solar to AC-in-2 | 4568 | uint32 | 100 | 0 to 42949672.96 | /Energy/SolarToAcIn2 | no | kWh
com.victronenergy.multi | Energy from solar to AC-out | 4570 | uint32 | 100 | 0 to 42949672.96 | /Energy/SolarToAcOut | no | kWh
com.victronenergy.multi | Energy from solar to battery | 4572 | uint32 | 100 | 0 to 42949672.96 | /Energy/SolarToBattery | no | kWh
com.victronenergy.multi | Yield today | 4574 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Yield | no | kWh
com.victronenergy.multi | Maximum charge power today | 4575 | uint16 | 1 | 0 to 65535 | /History/Daily/0/MaxPower | no | W
com.victronenergy.multi | Yield yesterday | 4576 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Yield | no | kWh
com.victronenergy.multi | Maximum charge power yesterday | 4577 | uint16 | 1 | 0 to 65535 | /History/Daily/1/MaxPower | no | W
com.victronenergy.multi | Yield today for tracker 0 | 4578 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/0/Yield | no | kWh
com.victronenergy.multi | Yield today for tracker 1 | 4579 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/1/Yield | no | kWh
com.victronenergy.multi | Yield today for tracker 2 | 4580 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/2/Yield | no | kWh
com.victronenergy.multi | Yield today for tracker 3 | 4581 | uint16 | 10 | 0 to 6553.5 | /History/Daily/0/Pv/3/Yield | no | kWh
com.victronenergy.multi | Yield yesterday for tracker 0 | 4582 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/0/Yield | no | kWh
com.victronenergy.multi | Yield yesterday for tracker 1 | 4583 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/1/Yield | no | kWh
com.victronenergy.multi | Yield yesterday for tracker 2 | 4584 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/2/Yield | no | kWh
com.victronenergy.multi | Yield yesterday for tracker 3 | 4585 | uint16 | 10 | 0 to 6553.5 | /History/Daily/1/Pv/3/Yield | no | kWh
com.victronenergy.multi | Maximum charge power today for tracker 0 | 4586 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/0/MaxPower | no | W
com.victronenergy.multi | Maximum charge power today for tracker 1 | 4587 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/1/MaxPower | no | W
com.victronenergy.multi | Maximum charge power today for tracker 2 | 4588 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/2/MaxPower | no | W
com.victronenergy.multi | Maximum charge power today for tracker 3 | 4589 | uint16 | 1 | 0 to 65535 | /History/Daily/0/Pv/3/MaxPower | no | W
com.victronenergy.multi | Maximum charge power yesterday tracker 0 | 4590 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/0/MaxPower | no | W
com.victronenergy.multi | Maximum charge power yesterday tracker 1 | 4591 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/1/MaxPower | no | W
com.victronenergy.multi | Maximum charge power yesterday tracker 2 | 4592 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/2/MaxPower | no | W
com.victronenergy.multi | Maximum charge power yesterday tracker 3 | 4593 | uint16 | 1 | 0 to 65535 | /History/Daily/1/Pv/3/MaxPower | no | W
com.victronenergy.multi | PV voltage for tracker 0 | 4594 | uint16 | 10 | 0 to 6553.5 | /Pv/0/V | no | V DC
com.victronenergy.multi | PV voltage for tracker 1 | 4595 | uint16 | 10 | 0 to 6553.5 | /Pv/1/V | no | V DC
com.victronenergy.multi | PV voltage for tracker 2 | 4596 | uint16 | 10 | 0 to 6553.5 | /Pv/2/V | no | V DC
com.victronenergy.multi | PV voltage for tracker 3 | 4597 | uint16 | 10 | 0 to 6553.5 | /Pv/3/V | no | V DC
com.victronenergy.multi | PV power for tracker 0 | 4598 | uint16 | 1 | 0 to 65535 | /Pv/0/P | no | W
com.victronenergy.multi | PV power for tracker 1 | 4599 | uint16 | 1 | 0 to 65535 | /Pv/1/P | no | W
com.victronenergy.multi | PV power for tracker 2 | 4600 | uint16 | 1 | 0 to 65535 | /Pv/2/P | no | W
com.victronenergy.multi | PV power for tracker 3 | 4601 | uint16 | 1 | 0 to 65535 | /Pv/3/P | no | W
com.victronenergy.multi | Low SOC alarm | 4602 | uint16 | 1 | 0 to 65535 | /Alarms/LowSoc | no | 0=No alarm;1=Warning;2=Alarm
com.victronenergy.multi | User yield | 4603 | uint32 | 1 | 0 to 4294967295 | /Yield/User | no | kWh | Energy generated by the solarcharger since last user reset
com.victronenergy.multi | MPP operation mode tracker 1 | 4605 | uint16 | 1 | 0 to 65535 | /Pv/0/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.multi | MPP operation mode tracker 2 | 4606 | uint16 | 1 | 0 to 65535 | /Pv/1/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.multi | MPP operation mode tracker 3 | 4607 | uint16 | 1 | 0 to 65535 | /Pv/2/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.multi | MPP operation mode tracker 4 | 4608 | uint16 | 1 | 0 to 65535 | /Pv/3/MppOperationMode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.multi | ESS mode | 4609 | uint16 | 1 | 0 to 65535 | /Settings/Ess/Mode | yes | 0=self-consumption (battery-life);1=self-consumption;2=Keep charged;3=External control
com.victronenergy.multi | ESS power setpoint | 4610 | int32 | 1 | -2147483648 to 2147483648 | /Ess/AcPowerSetpoint | yes | W
com.victronenergy.multi | Disable Feed-in | 4612 | uint16 | 1 | 0 to 65535 | /Ess/DisableFeedIn | yes | 0=Feed-in enabled;1=Feed-in disabled
com.victronenergy.multi | Disable charge | 4613 | uint16 | 1 | 0 to 65535 | /Ess/DisableCharge | yes | 0=Charge enabled;1=Charge disabled
com.victronenergy.multi | ESS Minimum SOC Limit | 4614 | uint16 | 1 | 0 to 65535 | /Settings/Ess/MinimumSocLimit | yes | %
com.victronenergy.multi | Sustain active | 4615 | uint16 | 1 | 0 to 65535 | /Ess/Sustain | no | 0=Sustain inactive; 1=Sustain active
com.victronenergy.multi | RESERVED | 4616
com.victronenergy.multi | RESERVED | 4617
com.victronenergy.multi | RESERVED | 4618
com.victronenergy.multi | RESERVED | 4619
com.victronenergy.multi | Short Circuit Alarm | 4620 | uint16 | 1 | 0 to 65535 | /Alarms/ShortCircuit | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.pump | Pump State | 4700 | uint16 | 1 | 0 to 65535 | /State | no | 0=Stopped;1=Running
com.victronenergy.settings | Auto start enabled | 4701 | uint16 | 1 | 0 to 65535 | /Settings/Pump0/AutoStartEnabled | yes | 0=Disabled;1=Enabled
com.victronenergy.settings | Mode | 4702 | uint16 | 1 | 0 to 65535 | /Settings/Pump0/Mode | yes | 0=Auto;1=On;2=Off
com.victronenergy.settings | Start value | 4703 | uint16 | 1 | 0 to 100 | /Settings/Pump0/StartValue | yes | %
com.victronenergy.settings | Stop value | 4704 | uint16 | 1 | 0 to 100 | /Settings/Pump0/StopValue | yes | %
com.victronenergy.dcdc | Product ID | 4800 | uint16 | 1 | 0 to 65535 | /ProductId | no
com.victronenergy.dcdc | Firmware version | 4801 | uint32 | 1 | 0 to 4294967295 | /FirmwareVersion | no
com.victronenergy.dcdc | Error code | 4803 | uint16 | 1 | 0 to 65535 | /ErrorCode | no | 0=No error;1=Battery temperature too high;2=Battery voltage too high;3=Battery temperature sensor miswired (+);4=Battery temperature sensor miswired (-);5=Battery temperature sensor disconnected;6=Battery voltage sense miswired (+);7=Battery voltage sense miswired (-);8=Battery voltage sense disconnected;9=Battery voltage wire losses too high;17=Charger temperature too high;18=Charger over-current;19=Charger current polarity reversed;20=Bulk time limit reached;22=Charger temperature sensor miswired;23=Charger temperature sensor disconnected;34=Input current too high
com.victronenergy.dcdc | Battery voltage | 4804 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | V DC
com.victronenergy.dcdc | Battery current | 4805 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | A DC
com.victronenergy.dcdc | Battery temperature | 4806 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Temperature | no | Degrees celsius
com.victronenergy.dcdc | Switch position | 4807 | uint16 | 1 | 0 to 65535 | /Mode | yes | 1=On;4=Off
com.victronenergy.dcdc | Charge state | 4808 | uint16 | 1 | 0 to 65535 | /State | no | 0=Off;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;11=Power Supply
com.victronenergy.dcdc | Input voltage (before DC/DC converter) | 4809 | uint16 | 100 | 0 to 655.35 | /Dc/In/V | no | V DC
com.victronenergy.dcdc | Input power | 4810 | uint16 | 1 | 0 to 65535 | /Dc/In/P | no | W
com.victronenergy.dcdc | Accumulated Ah converted | 4811 | uint16 | 10 | 0 to 6553.5 | /History/Cumulative/User/ChargedAh | no | Ah
com.victronenergy.acsystem | System state | 4900 | uint16 | 1 | 0 to 65535 | /State | no | 0=Off;1=Low Power;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;8=Passthru;9=Inverting;10=Power assist;11=Power supply;252=External control
com.victronenergy.acsystem | Input voltage phase 1 | 4901 | uint16 | 10 | 0 to 6553.5 | /Ac/In/1/L1/V | no | V AC
com.victronenergy.acsystem | Input voltage phase 2 | 4902 | uint16 | 10 | 0 to 6553.5 | /Ac/In/1/L2/V | no | V AC
com.victronenergy.acsystem | Input voltage phase 3 | 4903 | uint16 | 10 | 0 to 6553.5 | /Ac/In/1/L3/V | no | V AC
com.victronenergy.acsystem | Input current phase 1 | 4904 | int16 | 10 | 0 to 6553.5 | /Ac/In/1/L1/I | no | A AC
com.victronenergy.acsystem | Input current phase 2 | 4905 | int16 | 10 | 0 to 6553.5 | /Ac/In/1/L2/I | no | A AC
com.victronenergy.acsystem | Input current phase 3 | 4906 | int16 | 10 | 0 to 6553.5 | /Ac/In/1/L3/I | no | A AC
com.victronenergy.acsystem | Input power phase 1 | 4907 | int16 | 0.1 | -327680 to 327670 | /Ac/In/1/L1/P | no | W
com.victronenergy.acsystem | Input power phase 2 | 4908 | int16 | 0.1 | -327680 to 327670 | /Ac/In/1/L2/P | no | W
com.victronenergy.acsystem | Input power phase 3 | 4909 | int16 | 0.1 | -327680 to 327670 | /Ac/In/1/L3/P | no | W
com.victronenergy.acsystem | Input frequency | 4910 | uint16 | 100 | 0 to 655.35 | /Ac/In/1/L1/F | no | Hz
com.victronenergy.acsystem | Output voltage phase 1 | 4911 | uint16 | 10 | 0 to 6553.5 | /Ac/Out/L1/V | no | V AC
com.victronenergy.acsystem | Output voltage phase 2 | 4912 | uint16 | 10 | 0 to 6553.5 | /Ac/Out/L2/V | no | V AC
com.victronenergy.acsystem | Output voltage phase 3 | 4913 | uint16 | 10 | 0 to 6553.5 | /Ac/Out/L3/V | no | V AC
com.victronenergy.acsystem | Output current phase 1 | 4914 | int16 | 10 | -3276.8 to 3276.7 | /Ac/Out/L1/I | no | A AC
com.victronenergy.acsystem | Output current phase 2 | 4915 | int16 | 10 | -3276.8 to 3276.7 | /Ac/Out/L2/I | no | A AC
com.victronenergy.acsystem | Output current phase 3 | 4916 | int16 | 10 | -3276.8 to 3276.7 | /Ac/Out/L3/I | no | A AC
com.victronenergy.acsystem | Output power phase 1 | 4917 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L1/P | no | W
com.victronenergy.acsystem | Output power phase 2 | 4918 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L2/P | no | W
com.victronenergy.acsystem | Output power phase 3 | 4919 | int16 | 0.1 | -327680 to 327670 | /Ac/Out/L3/P | no | W
com.victronenergy.acsystem | Output frequency | 4920 | uint16 | 100 | 0 to 655.35 | /Ac/Out/L1/F | no | Hz
com.victronenergy.acsystem | ESS mode | 4921 | uint16 | 1 | 0 to 65535 | /Settings/Ess/Mode | yes | 1=ESS with Phase Compensation;2=ESS without phase compensation;3=Disabled/External Control
com.victronenergy.acsystem | ESS setpoint | 4922 | int32 | 1 | -2147483648 to 2147483648 | /Ess/AcPowerSetpoint | yes | W
com.victronenergy.acsystem | Disable Feed-in (into grid) | 4924 | uint16 | 1 | 0 to 65535 | /Ess/DisableFeedIn | yes | 0=Feed-in enabled;1=Feed-in disabled
com.victronenergy.acsystem | RESERVED | 4925
com.victronenergy.acsystem | RESERVED | 4926
com.victronenergy.acsystem | RESERVED | 4927
com.victronenergy.acsystem | RESERVED | 4928
com.victronenergy.acsystem | RESERVED | 4929
com.victronenergy.acsystem | Grid Lost Alarm | 4930 | uint16 | 1 | 0 to 65535 | /Alarms/GridLost | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.acsystem | Phase Rotation Alarm | 4931 | uint16 | 1 | 0 to 65535 | /Alarms/PhaseRotation | no | 0=Ok;1=Warning;2=Alarm
com.victronenergy.dcgenset | Genset Product ID | 5200 | uint16 | 1 | 0 to 65535 | /ProductId | no
com.victronenergy.dcgenset | Status | 5201 | uint16 | 1 | 0 to 65535 | /StatusCode | no
com.victronenergy.dcgenset | Error | 5202 | uint16 | 1 | 0 to 65535 | /ErrorCode | no
com.victronenergy.dcgenset | Auto start enabled | 5203 | uint16 | 1 | 0 to 65535 | /RemoteStartModeEnabled | no
com.victronenergy.dcgenset | Start generator | 5204 | uint16 | 1 | 0 to 65535 | /Start | yes | 0=Stop generator; 1=Start generator
com.victronenergy.dcgenset | DC voltage | 5205 | uint16 | 100 | 0 to 655.35 | /Dc/0/Voltage | no | DC V
com.victronenergy.dcgenset | DC current | 5206 | int16 | 10 | -3276.8 to 3276.7 | /Dc/0/Current | no | DC A
com.victronenergy.dcgenset | Engine load | 5207 | uint16 | 1 | 0 to 65535 | /Engine/Load | no | %
com.victronenergy.dcgenset | Heatsink temperature | 5208 | uint16 | 1 | 0 to 65535 | /Engine/Speed | no | RPM
com.victronenergy.dcgenset | Engine oil temperature | 5209 | uint16 | 0.01 | 0 to 6553500 | /Engine/OperatingHours | no | Seconds
com.victronenergy.dcgenset | Engine coolant temperature | 5210 | int16 | 10 | -3276.8 to 3276.7 | /Engine/CoolantTemperature | no | Degrees celsius
com.victronenergy.dcgenset | Internal winding temperature | 5211 | int16 | 10 | -3276.8 to 3276.7 | /Engine/WindingTemperature | no | Degrees celsius
com.victronenergy.dcgenset | Engine exhaust temperature | 5212 | int16 | 10 | -3276.8 to 3276.7 | /Engine/ExaustTemperature | no | Degrees celsius
com.victronenergy.dcgenset | Starter battery voltage | 5213 | uint16 | 100 | 0 to 655.35 | /StarterVoltage | no | DC V
com.victronenergy.dcgenset | Oil pressure | 5214 | int16 | 1 | -32768 to 32767 | /Engine/OilPressure | no | kPa
com.victronenergy.dcgenset | Heatsink temperature | 5215 | int16 | 10 | -3276.8 to 3276.7 | /HeatsinkTemperature | no | Degrees celsius
com.victronenergy.dcgenset | Engine oil temperature | 5216 | int16 | 1 | -32768 to 32767 | /Engine/OilTemperature | no | Degrees celsius
com.victronenergy.dcgenset | RESERVED | 5217 | uint16 | 1 |  | RESERVED | no
com.victronenergy.dcgenset | 1st Error string (for third party gensets) | 5218 | string[16] | 1 |  | /Error/0/Id | no | See https://github.com/victronenergy/venus/wiki/dbus#error-codes
com.victronenergy.dcgenset | 2nd Error string (for third party gensets) | 5234 | string[16] | 1 |  | /Error/1/Id | no
com.victronenergy.dcgenset | 3rd Error string (for third party gensets) | 5250 | string[16] | 1 |  | /Error/2/Id | no
com.victronenergy.dcgenset | 4th Error string (for third party gensets) | 5266 | string[16] | 1 |  | /Error/3/Id | no
com.victronenergy.dcgenset | 5th Error string (for third party gensets) | 5282 | string[16] | 1 |  | /Error/4/Id | no
com.victronenergy.dcgenset | 6th Error string (for third party gensets) | 5298 | string[16] | 1 |  | /Error/5/Id | no
com.victronenergy.dcgenset | 7th Error string (for third party gensets) | 5314 | string[16] | 1 |  | /Error/6/Id | no
com.victronenergy.dcgenset | 8th Error string (for third party gensets) | 5330 | string[16] | 1 |  | /Error/7/Id | no
com.victronenergy.system | Dynamic ESS state | 5400 | uint16 | 1 | 0 to 65535 | /DynamicEss/Active | no | 0=Off;1=Active
com.victronenergy.system | Allow grid feed-in | 5401 | uint16 | 1 | 0 to 65535 | /DynamicEss/AllowGridFeedIn | no | 0=Not allowed;1=Allowed
com.victronenergy.system | Is Dynamic ESS available | 5402 | uint16 | 1 | 0 to 65535 | /DynamicEss/Available | no | 0=System is not capable of doing DynamicEss;1=System is capable of doing DynamicEss
com.victronenergy.system | Calculated rate of charge/discharge | 5403 | uint16 | 0.1 | 0 to 655350 | /DynamicEss/ChargeRate | no
com.victronenergy.system | Error | 5404 | uint16 | 1 | 0 to 65535 | /DynamicEss/ErrorCode | no | 0=No error;1=No ESS;2=ESS mode;3=No matching schedule;4=SOC low;5=Battery capacity not configured
com.victronenergy.system | Active restrictions | 5405 | uint16 | 1 | 0 to 65535 | /DynamicEss/Restrictions | no | 0=No restrictions between battery and the grid;1=Grid to battery energy flow is restricted;2=Battery to grid energy flow is restricted;3=No energy flow between battery and grid
com.victronenergy.system | Used strategy for current time slot | 5406 | uint16 | 1 | 0 to 65535 | /DynamicEss/Strategy | no | 0=Target SOC;1=Self-consumption
com.victronenergy.system | The set target SOC for this time slot | 5407 | uint16 | 1 | 0 to 65535 | /DynamicEss/TargetSoc | no | %
com.victronenergy.settings | Battery capacity | 5420 | uint16 | 10 | 0 to 6553.5 | /Settings/DynamicEss/BatteryCapacity | yes | kWh
com.victronenergy.settings | Full battery charge duration | 5421 | uint16 | 1 | 0 to 65535 | /Settings/DynamicEss/FullChargeDuration | yes | hour
com.victronenergy.settings | Full battery charge interval | 5422 | uint16 | 1 | 0 to 65535 | /Settings/DynamicEss/FullChargeInterval | yes | day
com.victronenergy.settings | Dynamic ESS mode | 5423 | uint16 | 1 | 0 to 65535 | /Settings/DynamicEss/Mode | yes | 0=Off;1=Auto;4=Node-RED
com.victronenergy.settings | Allow grid feed-in during this schedule | 5424 | uint16 | 1 | 0 to 65535 | /Settings/DynamicEss/Schedule/0/AllowGridFeedIn | yes | 0=Not allowed;1=Allowed
com.victronenergy.settings | Duration for this schedule | 5425 | uint16 | 1 | 0 to 65535 | /Settings/DynamicEss/Schedule/0/Duration | yes | Seconds
com.victronenergy.settings | Active restrictions for this schedule | 5426 | uint16 | 1 | 0 to 65535 | /Settings/DynamicEss/Schedule/0/Restrictions | yes | 0=No restrictions between battery and the grid;1=Grid to battery energy flow is restricted;2=Battery to grid energy flow is restricted;3=No energy flow between battery and grid
com.victronenergy.settings | Target SOC for this schedule | 5427 | uint16 | 1 | 0 to 65535 | /Settings/DynamicEss/Schedule/0/Soc | yes | %
com.victronenergy.settings | Unix timestamp when this schedule starts | 5428 | int32 | 1 | -2147483648 to 2147483648 | /Settings/DynamicEss/Schedule/0/Start | yes
com.victronenergy.settings | Used strategy for this schedule | 5429 | uint16 | 1 | 0 to 65535 | /Settings/DynamicEss/Schedule/0/Strategy | yes | 0=Target SOC;1=Self-consumption

## Unit ID mapping
Unit ID | /DeviceInstance | Remark
100 | 0 | VE.Can device instance 0 and all registers listed as com.victronenergy.system
204 | 262
205 | 263
206 | 264
207 | 265
208 | 266
209 | 267
210 | 268
211 | 269
212 | 270
213 | 271
214 | 272
215 | 280
216 | 281
217 | 282
218 | 283
219 | 284
220 | 285
221 | 286
222 | 287
223 | 277 | Cerbo GX VE.Direct port 3 (ttyS5)
224 | 278 | Cerbo GX VE.Direct port 2 (ttyS6)
225 | 512 | CAN-bus BMS
226 | 279 | Cerbo GX VE.Direct port 1 (ttyS7)
227 | 276 | Cerbo GX VE.Bus port (ttyS4)
228 | 275 | EasySolar-II/Multiplus-II GX VE.Bus port (ttyS3)
229 | 274 | EasySolar-II/Multiplus-II GX VE.Direct port (ttyS2)
230 | 273 | EasySolar-II/Multiplus-II GX VE.Direct port (ttyS1)
231 | 295 | VE.Direct via USB, Octo GX VE.Direct 9 (ttyUSB7)
232 | 294 | VE.Direct via USB, Octo GX VE.Direct 8 (ttyUSB6)
233 | 293 | VE.Direct via USB, Octo GX VE.Direct 7 (ttyUSB5)
234 | 296 | VE.Direct via USB, Octo GX VE.Direct 10 (ttyUSB8)
235 | 292 | VE.Direct via USB, Octo GX VE.Direct 6 (ttyUSB4)
236 | 291 | VE.Direct via USB, Octo GX VE.Direct 5 (ttyUSB3)
237 | 290 | VE.Direct via USB, Octo GX VE.Direct 4 (ttyUSB2)
238 | 289 | VE.Direct via USB, Octo GX VE.Direct 3 (ttyUSB1)
239 | 288 | VE.Direct via USB (ttyUSB0)
242 | 261 | Venus GX VE.Bus port (ttyO5)
243 | 260 | Venus GX VE.Direct port 2, Octo GX port 2 (ttyO4)
244 | 259
245 | 258 | CCGX VE.Direct port 2, Venus GX VE.Direct port 1, Octo GX port 1 (ttyO2)
246 | 257 | CCGX VE.Bus port (ttyO1)
247 | 256 | CCGX VE.Direct 1 port (ttyO0)
Note on finding the modbus Unit ID
On the CCGX go to the device list and open the device of interest, then open the Device subsection. This section will have a device instance entry. Use this table to find the unit ID (column A) that matches the device instance (column B). In general the unit ID will be equal to the device instance, except when the device instance exceeds 247. If the device instance is 0 you can use both 0 and 100 as unit ID. Keep in mind that many modbus TCP clients do not support unit ID 0.

## Document versions
Rev 0 | Initial version
Rev 1 | Fixed numbering error: bmv state of charge and time to go both had id 266. Note that all bmv numbers higher than 266 have now been shifted one up!
Rev 2 | The shift of rev 1 has been undone: no shifting. So set time to go to 301, and leave the rest as it was in rev 0
Rev 3 | Changed the unitids, because some PLCs do not accept a modbustcp unitd above than 247:
VE-Bus port was 254, is now 246
VE.Direct port 1 was 255, is now 247
VE.Direct port 2 was 253, is now 245
Added com.victronenergy.charger: Skylla-i. Requires CCGX v1.16 or higher.
Rev 4 | Added Hub4 parameters (preliminary!)
Added device instance 10 to 12
Changed scaling of all battery parameters that are related to Ah (consumed Ah for example) from 10 to -10
Rev 5 | Updated Hub4 registers (vebus)
Added grid meter (com.victronenergy.grid) including registers to control hub-4 control loop\
Added gps (com.victronenergt.gps)
Renamed DC D-Bus paths (eg. /Dc/0/V to /Dc/0/Voltage).
Changed scaling of solar charger daily yield (address 784)
Added Unit ID's for PV inverters
Rev 6 | Added Hub-4 setpoints for phase 2 and 3.
Rev 7 | Added battery state of health
Added solar charger user yield
Added unit IDs for Redflow and LG batteries
Rev 8 | Added CAN.Bus BMS battery parameters
Added UnitID 100 (maps to UnitID 0)
Added system parameters (sum of all PV power, grid power,…)
Added relays
Added vebus multi phase alarms
Added vebus Temperature & Voltage sensor alarms
Added hub4 BatteryLife state
Added PV inverter disable flag
Rev 9 | Added remarks column in field list
Added some helpful information on finding the unit ID
Added VE.Bus BMS paths
Rev 10 | Added remark that unit ID is also used for system device
Added VE.Direct inverters
Added Fisher Panda generators
Added tank sensors
Added ESS grid power setpoint with a smaller scale factor (allows setting power > 32kW)
Added Lynx Ion BMS.
Note that in systems with both a Lynx Ion shunt and Lynx Ion bms, there will be 2 battery services now. One of them will have device instance 0, the other 1. In older CCGX firmwares, both could have device instance 0. In that case the modbus TCP user will have to change the unit ID: use unit ID 1 for all battery registers < 1200 instead of ID 0.
Rev 11 | Renamed hub-4 to ESS is descriptions and remarks
Rev 12 | Added Unit IDs for Venus GX tty ports
Added temperature sensors
Added ESS minimum SoC
Rev 13 | Added active input source
Added voltage and current readings to grid servce
Added support for reading digital inputs
Rev 14 | Put the system device on top, and removed references to unit-id 0 from the remarks of the com.victronenergy.system registers.
Rev 15 | Add ESS Mode 2 and 3 to the remarks of those registers
Some other small textual improvements.
Rev 16 | Added registers for battery alarms
Changed battery relay to be writeable (only works with some batteries).
Added LowCellVoltage alarm for Lynx batteries
Added VE.Bus temperature
Added VE.Bus reset
Rev 17 | Added registers for generator start/stop
Rev 18 | Added register for ESS mode
Added register for vebus phase rotation warning
Added register for solar charger’s MPP operation mode
Rev 19 | Added register for ESS mode 2 maximum discharge current
Added register for DVCC maximum system charge current
Rev 20 | Added 32-bit energy registers for PV-inverters
Rev 21 | Added registers for IMT solar irradiation sensors
Rev 22 | Moved 32-bit energy registers added in Rev-20 because they overlapped with the serial number
Rev 23 | Added register for GridLost alarm
Rev 24 | Added mapping for EasySolar-II/Multiplus-II GX VE.Bus port
Rev 25 | Added GPS Altitude
Rev 26 | Corrected Dbus path for generator ManualStart
Rev 27 | Add mappings for Cerbo GX ports
Rev 28 | Added mapping for EasySolar-II/Multiplus-II GX VE.Direct ports
Added mappings for up to 9 USB-connected VE.Direct devices
Added Octo-GX mappings
Rev 29 | GridLost alarm moved to the vebus service
Add register for maximum system grid feed in
Rev 30 | Added registers for AC-coupled and DC-coupled grid feed-in
Added register indicating whether Feed-in limiting is active
Added registers for feeding in overvoltage/excess DC-coupled power and limiting the amount
Added 32-bit register for generator runtime.
Rev 31 | Added additional registers for generator start/stop
Rev 32 | Corrected the allowed ranges for many of the registers
Rev 33 | Added registers for MPPTs with multiple trackers
Added register for Multi/Quattro IgnoreAcInput
Rev 34 | Add registers for EV-Charger
Add register for maximum charge voltage for a managed battery
Rev 35 | Corrected and added register for IgnoreAcIn1/2
Rev 36 | Updated battery /State & /Error values
Updated battery /Diagnostics/LastErrors/n/Error
Rev 37 | Add more registers related to Inverter RS Smart
Add missing registers for ESS mode 3 control of overvoltage feed-in
Rev 38 | Add registers for PV-inverter total power, max power and power limit
Add read-only register for ESS active SOC limit
Rev 39 | Add registers for acload service
Rev 40 | Correct definition of maximum charge voltage for managed battery
Add registers for fuel cell, dcload, dcsource, alternator and dcsystem services
Remove PV-side current values from solar chargers and replace them with more accurate power values
Remove PV-side current values from inverter RS and replace them with more accurate power values
Add registers for total energy measured by grid meters
Rev 41 | Add registers for Multi RS
Add registers for battery voltage and humidity on temperature sensors (Ruuvi)
Rev 42 | Restore PV-side current that was incorrectly removed also for older Solar Chargers
Add tracker history for Multi-RS
Add PV tracker voltage and power for multitracker Multi-RS
Update dbus paths for generator start-stop
Add register for EV charger position
Rev 43 | Add registers for VE.Bus Multi energy counters
Add registers for wakespeed alternators
Fix incorrect unit for PV-Inverter powerlimit register
Add new tank types to fluid type enum
Add additional diagnostic items for CAN-bms batteries
Add LowSoc alarm register for Inverter RS and Multi RS
Fix remarks for register 2903
Rev 44 | Document state 17 for battery state (Contactor check)
Add registers for pump-related controls
Add register for VE.Bus BMS (v2) pre-alarm
Add 32-bit registers for Multi-RS and SolarCharger total yield
Add register for VE.Bus charge state (similar to VE.Bus state, but provides additional info, and works better with managed batteries)
Add register for solarcharger power with scalefactor of 1 (up to 65kW)
Add registers for AC input source configuration (for VE.Bus Inverter/Chargers)
Add registers for genset engine oil pressure and fuel level
Rev 45 | Fix typo in AC-load service serial number register
Clean up Unit ID mapping, remove unnecessary mappings where modbus id equals Device Instance
Add mappings for device instances up to 296
Add 32-bit registers for ESS grid setpoint on vebus service
Add registers for PreferRenewableEnergy feature
Make ESS max discharge current (2704) int16 so it can take -1 (disabled) as value
Add registers for individual tracker MppOperationMode, MPPT RS, Inverter RS and Multi RS
Add registers for reading- and resetting generator service interval
Add 32-bit power registers for grid meters and PV-inverters
Correct typo in unit of measure for GPS Altitude
Rev 46 | Support second temperature sensor on meteo sensor
Document ve.bus State 244 – Sustain
Document prefered use of generator/ManualStart over genset/Start
Add registers for DC/DC converter
Add register for system time (UTC)
Add registers for vebus powerassistenabled, boost factor, output voltage
Rev 47 | Add more registers for alternators, eg Orion XS masquarading as alternator
Add register for VE.Bus redetection
Add registers for ESS function of Multi-RS
Add registers for VE.Bus Ups Function
Rev 48 | Add register for Multi RS ESS MinSocLimit
Add register for InverterCharger summary (hides distinction between VE.Bus Multi and Multi-RS)
Add regisers for acsystem service (a collection of RS devices)
Add registers for system input/output loads (similar to what is on the overview)
Replace the registers for PowerAssist, Boost Factor, Output voltage and UPS function with new better versions. The old version was broken in any case.
Add register for genset oil temperature
Add registers for SmartLithium specific values: Balancer state and error flags
Update enum for generator start/stop states
Rev 49 | Rename genset AutoStart dbus path to RemoteStartModeEnabled
Add registers for the genset error strings
Add register for Multi RS Sustain condition
Add register for battery connection information
Add registers for acsystem grid lost and phase rotation alarms
Fix broken genset AC frequency register
Add registers for DC-generators, such as those made by FischerPanda
Add registers for Dynamic ESS